## Summary
Copeland Digital Scroll characteristics.
◇Copeland Digital Scroll(R22 Refrigerant) was tested at xxx PAC.
This report summarize some parts of the test result
■ How the Digital Scroll works
1) At the full load operation
・Solenoid valve (Out side the compressor ) is closed.
・Biasing chamber pressure of the compressor is discharge pressure.
・Fixed Scroll is pressed to the Orbiting Scroll by the biasing chamber pressure.
2) At the unload operation
・Solenoid valve (Out side the compressor ) is open.
・Biasing chamber pressure of the compressor is suction pressure.
・Fixed Scroll is moved upward and makes axial clearance to the scroll teeth .
・The axial clearance to the scroll teeth cause unload operation.
3) Capacity control
To control the solenoid valve open and close time,
The digital scroll compressor is operated full load and unload.
If full load and unload operation time is same (10-10sec) , the capacity is controlled 50%.
and if the full load time is 6sec and unload time is 14sec, the capacity is controlled 30%.
■ Advantage points of the Digital Scroll
1) Capacity Control is available without INVERTER System.
(* Digital Scroll supplies with the SOLENOID VALVE and the piping.)
・Free from Higher harmonics problem of power supply.
2) Wide Capacity control range.
・5%-100% is available (Copeland information)
■ Disadvantage points of Digital Scroll
1) Low COP at the low capacity operating condition (Compared with Inverter compr.)
・xxx PAC test result shows large COP difference at the low capacity
operating condition.
2) Noise
・Noise level changes at the full load and unload operation.
This cyclic change noise is irritable.(xxx PAC feeling)
Full load noise is high frequency tone and Unload noise is low frequency tone.
Cycle time is 10-20sec (depends on the Capacity control quantity )
■ Additional information
1) Indoor flow temperature Drift is 0.3-0.8℃ at xxx PAC test and it is acceptable.
2) COPELAND appeals the high dehumidify capacity at low capacity operating
condition, but the actual date was same as Inverter system.

## Test Result 1.13c
Copeland Digital Scroll System Testing Result
1.Test System
・Compressor ：ZRP72KC-TF5 (Copeland Digital Scroll R22 ＰＷＭ10-100%) (drop in)
・Unit：PUH-J160GA/PLZ-J160AA 5m
Comparison System
・Compressor ：AxxxxF (xxx Inverter Scroll R22 20-120Ｈｚ) (drop in)
・Unit：PUZ-J160GAP/PLZ-J160AA 5m
2.Test Result
1) Cooling Condition COP
Cooling Capacity (kW) | 0.595 | 4.064 | 5.691 | 6.439 | 8.149 | 11.798 | 15.011 | 4.25 | 6.37 | 12 | 15
Copeland | 0.33 | 1.58 | 1.86 | 2 | 2.12 | 2.24 | 2.13
MITSUBISHI INV. | [7 empty] | 5.5 | 5.16 | 3.6 | 2.84
2) Heating Condition COP
Cooling Capacity (kW) | 0.904 | 4.321 | 6.464 | 7.575 | 9.494 | 13.834 | 18.983 | 3.66 | 5.49 | 10.693 | 14.601 | 16.5
Copeland | 0.89 | 2.4 | 2.59 | 2.72 | 2.84 | 2.8 | 2.63
MITSUBISHI INV. | [7 empty] | 5.5 | 5.24 | 4.3 | 3.7 | 3.25
3.Conclusion
Copeland Digital Scroll Compressor System COP is lower than
xxx DC inverter Scroll compressor system.
Especially, the low capacity operating COP difference is large.

## Structure
Copeland Digital Scroll Structure
Fixed Scroll move to upward
large clearance