## export
ModbusManager 1.0.8
20170215
Product: F1155, F1255
Database: 6859
Title | Info | ID | Unit | Size | Factor | Min | Max | Default | Mode
BT1 Outdoor temp | Outdoor temperature | 40004 | °C | s16 | 10 | 0 | 0 | 0 | R
EP23-BT2 Supply temp S4 | Supply temperature for system 4 | 40005 | °C | s16 | 10 | 0 | 0 | 0 | R
EP22-BT2 Supply temp S3 | Supply temperature for system 3 | 40006 | °C | s16 | 10 | 0 | 0 | 0 | R
EP21-BT2 Supply temp S2 | Supply temperature for system 2 | 40007 | °C | s16 | 10 | 0 | 0 | 0 | R
BT2 Supply temp S1 | Supply temperature for system 1 | 40008 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT3 Return temp | Return temperature | 40012 | °C | s16 | 10 | 0 | 0 | 0 | R
BT7 Hot Water top |  | 40013 | °C | s16 | 10 | 0 | 0 | 0 | R
BT6 Hot Water load |  | 40014 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT10 Brine in temp |  | 40015 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT11 Brine out temp |  | 40016 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT12 Cond. out |  | 40017 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT14 Hot gas temp |  | 40018 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT15 Liquid line |  | 40019 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT17 Suction |  | 40022 | °C | s16 | 10 | 0 | 0 | 0 | R
BT20 Exhaust air temp. 1 |  | 40025 | °C | s16 | 10 | 0 | 0 | 0 | R
BT21 Vented air temp. 1 |  | 40026 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT26 Temp Collector in FLM 1 | Connected to the FLM module | 40028 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT27 Temp Collector out FLM 1 | Connected to the FLM module | 40029 | °C | s16 | 10 | 0 | 0 | 0 | R
EP23-BT50 Room Temp S4 |  | 40030 | °C | s16 | 10 | 0 | 0 | 0 | R
EP22-BT50 Room Temp S3 |  | 40031 | °C | s16 | 10 | 0 | 0 | 0 | R
EP21-BT50 Room Temp S2 |  | 40032 | °C | s16 | 10 | 0 | 0 | 0 | R
BT50 Room Temp S1 |  | 40033 | °C | s16 | 10 | 0 | 0 | 0 | R
CL11-BT51 Pool 1 Temp |  | 40042 | °C | s16 | 10 | 0 | 0 | 0 | R
BT53 Solar Panel Temp | Used in Solar and AHPS Docking accessories | 40043 | °C | s16 | 10 | 0 | 0 | 0 | R
BT54 Solar Load Temp | Used in Solar and AHPS Docking accessories | 40044 | °C | s16 | 10 | 0 | 0 | 0 | R
EQ1-BT64 Cool Supply Temp |  | 40045 | °C | s16 | 10 | 0 | 0 | 0 | R
EQ1-BT65 Cool Return Temp |  | 40046 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-FD1 Temperature limiter |  | 40054 |  | s16 | 1 | 0 | 0 | 0 | R
BT1 Average | EB100-BT1 Outdoor temperature average | 40067 | °C | s16 | 10 | 0 | 0 | 0 | R
EM1-BT52 Boiler temperature | Temperature of Boiler | 40070 | °C | s16 | 10 | 0 | 0 | 0 | R
BT25 external supply temp |  | 40071 | °C | s16 | 10 | 0 | 0 | 0 | R
BF1 EP14 Flow | Current flow EP14¦Current flow EP15 | 40072 | l/m | s16 | 10 | 0 | 0 | 0 | R
EB100-FR1 Anode Status |  | 40074 |  | s16 | 1 | 0 | 0 | 0 | R
BT22 Supply air temp. |  | 40075 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BE3 Current Phase 3 |  | 40079 | A | s32 | 10 | 0 | 0 | 0 | R
EB100-BE2 Current Phase 2 |  | 40081 | A | s32 | 10 | 0 | 0 | 0 | R
EB100-BE1 Current Phase 1 |  | 40083 | A | s32 | 10 | 0 | 0 | 0 | R
CL12-BT51 Pool 2 Temp |  | 40106 | °C | s16 | 10 | 0 | 0 | 0 | R
BT20 Exhaust air temp. 4 |  | 40107 | °C | s16 | 10 | 0 | 0 | 0 | R
BT20 Exhaust air temp. 3 |  | 40108 | °C | s16 | 10 | 0 | 0 | 0 | R
BT20 Exhaust air temp. 2 |  | 40109 | °C | s16 | 10 | 0 | 0 | 0 | R
BT21 Vented air temp. 4 |  | 40110 | °C | s16 | 10 | 0 | 0 | 0 | R
BT21 Vented air temp. 3 |  | 40111 | °C | s16 | 10 | 0 | 0 | 0 | R
BT21 Vented air temp. 2 |  | 40112 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ4-BT26 Temp Collector in FLM 4 | Connected to the FLM module | 40113 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ3-BT26 Temp Collector in FLM 3 | Connected to the FLM module | 40114 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ2-BT26 Temp Collector in FLM 2 | Connected to the FLM module | 40115 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ4-BT27 Temp Collector out FLM 4 | Connected to the FLM module | 40116 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ3-BT27 Temp Collector out FLM 3 | Connected to the FLM module | 40117 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ2-BT27 Temp Collector out FLM 2 | Connected to the FLM module | 40118 | °C | s16 | 10 | 0 | 0 | 0 | R
EP23-BT3 Return temp S4 | Return temperature for system 4 | 40127 | °C | s16 | 10 | 0 | 0 | 0 | R
EP22-BT3 Return temp S3 | Return temperature for system 3 | 40128 | °C | s16 | 10 | 0 | 0 | 0 | R
EP21-BT3 Return temp S2 | Return temperature for system 2 | 40129 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT29 Compressor oil temperature |  | 40146 | °C | s16 | 10 | 0 | 0 | 0 | R
BT70 HW Comfort Supply Temp. | Hot water comfort supply temperature | 40147 | °C | s16 | 10 | 0 | 0 | 0 | R
EQ1-BT57 Collector temp. | External collector temperature for ACS | 40155 | °C | s16 | 10 | 0 | 0 | 0 | R
EQ1-BT75 Heatdump temp. | Heating medium dump temperature for ACS | 40156 | °C | s16 | 10 | 0 | 0 | 0 | R
EP27-BT2 Supply temp S8 | Supply temperature for system 8 | 40159 | °C | s16 | 10 | 0 | 0 | 0 | R
EP26-BT2 Supply temp S7 | Supply temperature for system 7 | 40160 | °C | s16 | 10 | 0 | 0 | 0 | R
EP25-BT2 Supply temp S6 | Supply temperature for system 6 | 40161 | °C | s16 | 10 | 0 | 0 | 0 | R
EP24-BT2 Supply temp S5 | Supply temperature for system 5 | 40162 | °C | s16 | 10 | 0 | 0 | 0 | R
EP27-BT3 Return temp S8 | Return temperature for system 8 | 40163 | °C | s16 | 10 | 0 | 0 | 0 | R
EP26-BT3 Return temp S7 | Return temperature for system 7 | 40164 | °C | s16 | 10 | 0 | 0 | 0 | R
EP25-BT3 Return temp S6 | Return temperature for system 6 | 40165 | °C | s16 | 10 | 0 | 0 | 0 | R
EP24-BT3 Return temp S5 | Return temperature for system 5 | 40166 | °C | s16 | 10 | 0 | 0 | 0 | R
EP27-BT50 Room Temp S8 |  | 40167 | °C | s16 | 10 | 0 | 0 | 0 | R
EP26-BT50 Room Temp S7 |  | 40168 | °C | s16 | 10 | 0 | 0 | 0 | R
EP25-BT50 Room Temp S6 |  | 40169 | °C | s16 | 10 | 0 | 0 | 0 | R
EP24-BT50 Room Temp S5 |  | 40170 | °C | s16 | 10 | 0 | 0 | 0 | R
BT1 Average, 1h | EB100-BT1 Outdoor temperature average, 1h | 40185 | °C | s16 | 10 | 0 | 0 | 0 | R
EP23-BT50 Room Temp S4 Average |  | 40188 | °C | s16 | 10 | 0 | 0 | 0 | R
EP27-BT50 Room Temp S8 Average |  | 40189 | °C | s16 | 10 | 0 | 0 | 0 | R
EP26-BT50 Room Temp S7 Average |  | 40190 | °C | s16 | 10 | 0 | 0 | 0 | R
EP25-BT50 Room Temp S6 Average |  | 40191 | °C | s16 | 10 | 0 | 0 | 0 | R
EP24-BT50 Room Temp S5 Average |  | 40192 | °C | s16 | 10 | 0 | 0 | 0 | R
EP22-BT50 Room Temp S3 Average |  | 40193 | °C | s16 | 10 | 0 | 0 | 0 | R
EP21-BT50 Room Temp S2 Average |  | 40194 | °C | s16 | 10 | 0 | 0 | 0 | R
BT50 Room Temp S1 Average |  | 40195 | °C | s16 | 10 | 0 | 0 | 0 | R
BT74 Average | BT74 heating cooling sensor average | 40212 | °C | s16 | 10 | 0 | 0 | 0 | R
BT25 Ext. supply temp, cooling |  | 40216 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S8 |  | 40217 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S7 |  | 40218 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S6 |  | 40219 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S5 |  | 40220 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S8 |  | 40221 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S7 |  | 40222 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S6 |  | 40223 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S5 |  | 40224 | °C | s16 | 10 | 0 | 0 | 0 | R
Mixing valve state S8 | Current | 40305 |  | u8 | 1 | 0 | 0 | 0 | R
Mixing valve state S7 | Current | 40306 |  | u8 | 1 | 0 | 0 | 0 | R
Mixing valve state S6 | Current | 40307 |  | u8 | 1 | 0 | 0 | 0 | R
Mixing valve state S5 | Current | 40308 |  | u8 | 1 | 0 | 0 | 0 | R
Inverter limit status |  | 40316 |  | u8 | 1 | 0 | 0 | 0 | R
Compressor Frequency, Request | The compressor frequency that has been requested by the system | 40321 | Hz | u16 | 1 | 0 | 0 | 0 | R
Max Compr. freq. | The maximum frequency of the compressor | 40322 | Hz | u16 | 100 | 0 | 0 | 0 | R
Inverter alarm code |  | 40323 |  | u16 | 1 | 0 | 0 | 0 | R
Inverter drive command |  | 40326 |  | u16 | 1 | 0 | 0 | 0 | R
NIBE Inverter Pic version |  | 40327 |  | u16 | 1 | 0 | 0 | 0 | R
NIBE Inverter 8051 version |  | 40328 |  | u16 | 1 | 0 | 0 | 0 | R
NIBE Inverter Def. Wizard |  | 40329 |  | u16 | 1 | 0 | 0 | 0 | R
NIBE Inverter Mce version |  | 40330 |  | u16 | 1 | 0 | 0 | 0 | R
NIBE Inverter Hw version |  | 40331 |  | u16 | 1 | 0 | 0 | 0 | R
NIBE Inverter Hw type |  | 40332 |  | u16 | 1 | 0 | 0 | 0 | R
External adjustment activated via input S8 |  | 40339 |  | u8 | 1 | 0 | 0 | 0 | R
External adjustment activated via input S7 |  | 40340 |  | u8 | 1 | 0 | 0 | 0 | R
External adjustment activated via input S6 |  | 40341 |  | u8 | 1 | 0 | 0 | 0 | R
External adjustment activated via input S5 |  | 40342 |  | u8 | 1 | 0 | 0 | 0 | R
Extra heating system pump S8 |  | 40365 |  | u8 | 1 | 0 | 0 | 0 | R
Extra heating system pump S7 |  | 40366 |  | u8 | 1 | 0 | 0 | 0 | R
Extra heating system pump S6 |  | 40367 |  | u8 | 1 | 0 | 0 | 0 | R
Extra heating system pump S5 |  | 40368 |  | u8 | 1 | 0 | 0 | 0 | R
Extra cooling HPAC, ACS |  | 40369 |  | u8 | 1 | 0 | 0 | 0 | R
BT82 HW Comfort Return Temp |  | 40625 | °C | s16 | 10 | 0 | 0 | 0 | R
BT83 HW Comfort Cylinder Temp |  | 40626 | °C | s16 | 10 | 0 | 0 | 0 | R
Tot. ext. HW add op.time | Total external hw-electric additive operation time | 40755 | h | s32 | 10 | 0 | 9999999 | 0 | R
Accumulated Energy Pool2 Cpr EP14 |  | 40771 | kWh | u32 | 10 | 0 | 9999999 | 0 | R
BM1 Humidity |  | 40834 | % | u16 | 10 | 0 | 0 | 0 | R
BM1 BT50 Room temp. |  | 40856 | °C | s16 | 10 | 0 | 0 | 0 | R
BM1 Pressure |  | 40857 | kPa | s16 | 10 | 0 | 0 | 0 | R
BM1 Dewpoint |  | 40858 | °C | s16 | 10 | 0 | 0 | 0 | R
#NAME? |  | 40868 | 1 | u8 | 1 | 0 | 0 | 0 | R
#NAME? | Tells if plusadjust system calls for heat or cool | 40870 |  | u8 | 1 | 0 | 0 | 0 | R
#NAME? | Which comfort mode | 40871 |  | u8 | 1 | 0 | 0 | 0 | R
#NAME? | requested adjustment | 40872 |  | s8 | 1 | 0 | 0 | 0 | R
#NAME? | Humidity | 40873 | %RH | s16 | 10 | 0 | 0 | 0 | R
#NAME? | Average of all room sensors | 40874 | °C | s16 | 10 | 0 | 0 | 0 | R
#NAME? | Outdoor temp | 40875 | °C | s16 | 10 | 0 | 0 | 0 | R
#NAME? | PCA input version | 40876 |  | u16 | 1 | 0 | 0 | 0 | R
#NAME? | If plusadjust accessory is activated | 40877 |  | u8 | 1 | 0 | 0 | 0 | R
#NAME? | If plusadjust system calls for heat | 40878 |  | u8 | 1 | 0 | 0 | 0 | R
BT64 Average | BT64 Cooling supply average | 40889 | °C | s16 | 10 | 0 | 0 | 0 | R
State ACS thermostat | The state of the ACS thermostat accessory | 40912 |  | u8 | 1 | 0 | 0 | 0 | R
State ACS term. heatdump | The state of the heatdump in the ACS thermostat accessory | 40913 |  | u8 | 1 | 0 | 0 | 0 | R
Degree Minutes |  | 40940 |  | s32 | 10 | -30000 | 30000 | 0 | R/W
Inverter min speed |  | 40993 |  | u16 | 1 | 0 | 0 | 0 | R
Inverter max speed |  | 40994 |  | u16 | 1 | 0 | 0 | 0 | R
Accumulated energy external energy meter 2 |  | 40995 | kWh | u32 | 100 | 0 | 2147483647 | 0 | R
Accumulated energy external energy meter 1 |  | 40997 | kWh | u32 | 100 | 0 | 2147483647 | 0 | R
Software version |  | 43001 |  | u16 | 1 | 0 | 0 | 0 | R
Degree Minutes (16 bit) |  | 43005 |  | s16 | 10 | -30000 | 30000 | 0 | R/W
Calculated Supply Temperature S4 |  | 43006 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S3 |  | 43007 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S2 |  | 43008 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S1 |  | 43009 | °C | s16 | 10 | 0 | 0 | 0 | R
Freeze Protection Status | 1 = Freeze protection active | 43013 |  | u8 | 1 | 0 | 0 | 0 | R
Status Cooling | 0=Off 1=On | 43024 |  | u8 | 1 | 0 | 0 | 0 | R
Tot. op.time add. | Total electric additive operation time | 43081 | h | s32 | 10 | 0 | 1000000 | 0 | R
Int. el.add. Power | Current power from the internal electrical addition | 43084 | kW | s16 | 100 | 0 | 0 | 0 | R
Prio | Indicates what heating action (HW/heat/pool) currently prioritised 10=Off 20=Hot Water 30=Heat 40=Pool 41=Pool 2 50=Transfer 60=Cooling | 43086 |  | u8 | 1 | 0 | 0 | 0 | R
Int. el.add. State | State of the internal electrical addition | 43091 |  | u8 | 1 | 0 | 0 | 0 | R
Mixing valve state S4 | Current state of the climate system mixing valve for system 4 | 43093 |  | u8 | 1 | 0 | 0 | 0 | R
Mixing valve state S3 | Current state of the climate system mixing valve for system 3 | 43094 |  | u8 | 1 | 0 | 0 | 0 | R
Mixing valve state S2 | Current state of the climate system mixing valve for system 2 | 43095 |  | u8 | 1 | 0 | 0 | 0 | R
Mixing valve state S1 | Current state of the climate system mixing valve for system 1 | 43096 |  | u8 | 1 | 0 | 0 | 0 | R
Status of the shunt controlled additional heat accessory | 10 = Off, 20 = Running, 30 = Passive | 43097 |  | u8 | 1 | 0 | 0 | 0 | R
HPAC state | State of the HPAC cooling accessory. | 43103 |  | u8 | 1 | 0 | 0 | 0 | R
Fan speed current | The current fan speed after scheduling and blocks are considered | 43108 | % | u8 | 1 | 0 | 0 | 0 | R
Compr. current min.freq. | The current minimum frequency of the compressor | 43122 | Hz | s16 | 1 | 0 | 0 | 0 | R
Compr. current max.freq. | The current maximum frequency of the compressor | 43123 | Hz | s16 | 1 | 0 | 0 | 0 | R
Compressor Frequency, Actual | The compressor frequency the compressor is currently running at | 43136 | Hz | u16 | 10 | 0 | 0 | 0 | R
Inverter Temperature | Current inverter temparture | 43140 | °C | s16 | 10 | 0 | 0 | 0 | R
Internal cooling blocked |  | 43152 |  | u8 | 1 | 0 | 0 | 0 | R
External adjustment activated via input S4 |  | 43158 |  | u8 | 1 | 0 | 0 | 0 | R
External adjustment activated via input S3 |  | 43159 |  | u8 | 1 | 0 | 0 | 0 | R
External adjustment activated via input S2 |  | 43160 |  | u8 | 1 | 0 | 0 | 0 | R
External adjustment activated via input S1 |  | 43161 |  | u8 | 1 | 0 | 0 | 0 | R
Blocking status of the shunt controlled add heat acc | 0 = Unblocked, 1 = Blocked | 43163 |  | u8 | 1 | 0 | 0 | 0 | R
Cooling blocked | Whether cooling is blocked | 43164 |  | u8 | 1 | 0 | 0 | 0 | R
Blocking status of the step controlled add heat acc | 0 = Unblocked, 1 = Blocked | 43171 |  | u8 | 1 | 0 | 0 | 0 | R
Hot Water Circulation Status GP11 |  | 43180 |  | u8 | 1 | 0 | 0 | 0 | R
Compressor Frequency, Target | The targeted compressor frequency, before excluding any blocked frequencies | 43182 | Hz | u16 | 1 | 0 | 0 | 0 | R
Tot. HW op.time add. | Total electric additive operation time in hot water mode | 43239 | h | s32 | 10 | 0 | 9999999 | 0 | R
HPAC Relays | Indicates the active relays on the HPAC accessory. The information is binary encoded | 43395 |  | u8 | 1 | 0 | 0 | 0 | R
Compressor starts EB100-EP14 | Number of compressorer starts | 43416 |  | s32 | 1 | 0 | 9999999 | 0 | R
Tot. op.time compr. EB100-EP14 | Total compressorer operation time | 43420 | h | s32 | 1 | 0 | 9999999 | 0 | R
Tot. HW op.time compr. EB100-EP14 | Total compressorer operation time in hot water mode | 43424 | h | s32 | 1 | 0 | 9999999 | 0 | R
Compressor State EP14 | 20 = Stopped, 40 = Starting, 60 = Running, 100 = Stopping | 43427 |  | u8 | 1 | 0 | 0 | 0 | R
Supply Pump State EP14 | State of the supply pump | 43431 |  | u8 | 1 | 0 | 0 | 0 | R
Brine pump state EP14 |  | 43433 |  | u8 | 1 | 0 | 0 | 0 | R
Compressor status EP14 | Indicates if the compressor is supplied with power 0=Off 1=On | 43435 |  | u8 | 1 | 0 | 0 | 0 | R
HM-pump Status EP14 | Status of the circ. pump | 43437 | % | u8 | 1 | 0 | 0 | 0 | R
Brinepump Status EP14 | Status of the Brine pump | 43439 | % | u8 | 1 | 0 | 0 | 0 | R
FLM 4 Cooling Status | Whether FLM cooling is active, 1=yes, 0=no | 43484 |  | u8 | 1 | 0 | 0 | 0 | R
FLM 3 Cooling Status | Whether FLM cooling is active, 1=yes, 0=no | 43485 |  | u8 | 1 | 0 | 0 | 0 | R
FLM 2 Cooling Status | Whether FLM cooling is active, 1=yes, 0=no | 43486 |  | u8 | 1 | 0 | 0 | 0 | R
FLM 1 Cooling Status | Whether FLM cooling is active, 1=yes, 0=no | 43487 |  | u8 | 1 | 0 | 0 | 0 | R
PCA-Base Relays EP14 | Indicates the active relays on the PCA-Base card. The information is binary encoded | 43514 |  | u8 | 1 | 0 | 0 | 0 | R
PCA-Power Relays EP14 | Indicates the active relays on the PCA-Power card. The information is binary encoded | 43516 |  | u8 | 1 | 0 | 0 | 0 | R
Calculated supply air temp. |  | 43542 | °C | s16 | 10 | 0 | 0 | 0 | R
Pool 2 blocked |  | 43560 |  | u8 | 1 | 0 | 0 | 0 | R
Pool 1 blocked |  | 43561 |  | u8 | 1 | 0 | 0 | 0 | R
Pool 2 valve |  | 43563 |  | u8 | 1 | 0 | 0 | 0 | R
Pool 1 valve |  | 43564 |  | u8 | 1 | 0 | 0 | 0 | R
Cool Degree Minutes |  | 44266 |  | s16 | 10 | -30000 | 30000 | 0 | R/W
Calc. Cooling Supply Temperature S4 |  | 44267 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S3 |  | 44268 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S2 |  | 44269 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S1 |  | 44270 | °C | s16 | 10 | 0 | 0 | 0 | R
State ACS | The state of the ACS accessory | 44276 |  | u8 | 1 | 0 | 0 | 0 | R
State ACS heatdump | The state of the heatdump in the ACS accessory | 44277 |  | u8 | 1 | 0 | 0 | 0 | R
State ACS cooldump | The state of the cooldump in the ACS accessory | 44278 |  | u8 | 1 | 0 | 0 | 0 | R
Accumulated Energy HW Cpr and Add EP14 |  | 44298 | kWh | u32 | 10 | 0 | 9999999 | 0 | R
Accumulated Energy Heat Cpr and Add EP14 |  | 44300 | kWh | u32 | 10 | 0 | 9999999 | 0 | R
Accumulated Energy Cooling Cpr EP14 |  | 44302 | kWh | u32 | 10 | 0 | 9999999 | 0 | R
Accumulated Energy Pool Cpr EP14 |  | 44304 | kWh | u32 | 10 | 0 | 9999999 | 0 | R
Accumulated Energy HW Cpr EP14 |  | 44306 | kWh | u32 | 10 | 0 | 9999999 | 0 | R
Accumulated energy Heat Cpr EP14 |  | 44308 | kWh | u32 | 10 | 0 | 9999999 | 0 | R
Software release |  | 44331 |  | u8 | 1 | 0 | 0 | 0 | R
Extra heating system pump S4 |  | 44744 |  | u8 | 1 | 0 | 0 | 0 | R
Extra heating system pump S3 |  | 44745 |  | u8 | 1 | 0 | 0 | 0 | R
Extra heating system pump S2 |  | 44746 |  | u8 | 1 | 0 | 0 | 0 | R
Pool 2 pump |  | 44748 |  | u8 | 1 | 0 | 0 | 0 | R
Pool 1 pump |  | 44749 |  | u8 | 1 | 0 | 0 | 0 | R
ACS valve |  | 44751 |  | u8 | 1 | 0 | 0 | 0 | R
ACS dump signal GP20 |  | 44752 |  | u8 | 1 | 0 | 0 | 0 | R
Passiv cool shunt |  | 44753 |  | u8 | 1 | 0 | 0 | 0 | R
Passiv cool pool |  | 44754 |  | u8 | 1 | 0 | 0 | 0 | R
State ground water pump |  | 44756 |  | u8 | 1 | 0 | 0 | 0 | R
State SG Ready |  | 44874 |  | u8 | 1 | 0 | 0 | 0 | R
SG Ready input A |  | 44878 |  | u8 | 1 | 0 | 0 | 0 | R
SG Ready input B |  | 44879 |  | u8 | 1 | 0 | 0 | 0 | R
Smart Price Adaption Heating Offset |  | 44896 |  | s8 | 10 | 0 | 0 | 0 | R
Smart Price Adaption HW Comfort Mode | 0=Eco,1=Normal,2=Luxury,10=Normal+,20=Mini | 44897 |  | s8 | 1 | 0 | 0 | 0 | R
Smart Price Adaption Pool Offset |  | 44898 |  | s8 | 1 | 0 | 0 | 0 | R
Smart Price Adaption Cool Offset |  | 44899 |  | s8 | 1 | 0 | 0 | 0 | R
State smart price adaption |  | 44908 |  | u8 | 1 | 0 | 0 | 0 | R
Brine pump auto controlled | Brine pump auto controlled | 44912 |  | s8 | 1 | 0 | 1 | 1 | R
Alarm Number | The value indicates the most severe current alarm | 45001 |  | s16 | 1 | 0 | 0 | 0 | R
Floor drying timer |  | 47291 | hrs | u16 | 1 | 0 | 10000 | 0 | R
Step controlled add. max. step | Maximum number of steps allowed in step controlled add. | 47325 |  | u8 | 1 | 0 | 7 | 3 | R
#NAME? |  | 40879 | 1 | s8 | 1 | 1 | 10 | 5 | R/W
#NAME? | Largest allowed change | 40880 |  | s8 | 1 | 0 | 0 | 0 | R/W
#NAME? | system7 affected by parallell chan | 40881 |  | u8 | 1 | 0 | 1 | 0 | R/W
#NAME? | system7 affected by parallell chan | 40882 |  | u8 | 1 | 0 | 1 | 0 | R/W
#NAME? | system6 affected by parallell change | 40883 |  | u8 | 1 | 0 | 1 | 0 | R/W
#NAME? | system5 affected by parallell change | 40884 |  | u8 | 1 | 0 | 1 | 0 | R/W
#NAME? | system4 affected by parallell change | 40885 |  | u8 | 1 | 0 | 1 | 0 | R/W
#NAME? | system3 affected by parallell change | 40886 |  | u8 | 1 | 0 | 1 | 0 | R/W
#NAME? | system2 affected by parallell change | 40887 |  | u8 | 1 | 0 | 1 | 0 | R/W
#NAME? | system1 affected by parallell change | 40888 |  | u8 | 1 | 0 | 1 | 0 | R/W
Reset Alarms |  | 45171 |  | u8 | 1 | 0 | 0 | 0 | R/W
Heat curve S4 | Heat curve to use see manual for the different curves. | 47004 |  | s8 | 1 | 0 | 15 | 9 | R/W
Heat curve S3 | Heat curve to use see manual for the different curves. | 47005 |  | s8 | 1 | 0 | 15 | 9 | R/W
Heat curve S2 | Heat curve to use see manual for the different curves. | 47006 |  | s8 | 1 | 0 | 15 | 9 | R/W
Heat curve S1 | Heat curve to use see manual for the different curves. | 47007 |  | s8 | 1 | 0 | 15 | 9 | R/W
Offset S4 | Offset of the heat curve | 47008 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S3 | Offset of the heat curve | 47009 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S2 | Offset of the heat curve | 47010 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S1 | Offset of the heat curve | 47011 |  | s8 | 1 | -10 | 10 | 0 | R/W
Min Supply System 4 |  | 47012 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 3 |  | 47013 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 2 |  | 47014 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 1 |  | 47015 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Max Supply System 4 |  | 47016 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 3 |  | 47017 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 2 |  | 47018 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 1 |  | 47019 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Own Heating Curve P7 | User defined heating curve point | 47020 | °C | s8 | 1 | 5 | 70 | 15 | R/W
Own Heating Curve P6 | User defined heating curve point | 47021 | °C | s8 | 1 | 5 | 70 | 15 | R/W
Own Heating Curve P5 | User defined heating curve point | 47022 | °C | s8 | 1 | 5 | 70 | 26 | R/W
Own Heating Curve P4 | User defined heating curve point | 47023 | °C | s8 | 1 | 5 | 70 | 32 | R/W
Own Heating Curve P3 | User defined heating curve point | 47024 | °C | s8 | 1 | 5 | 70 | 35 | R/W
Own Heating Curve P2 | User defined heating curve point | 47025 | °C | s8 | 1 | 5 | 70 | 40 | R/W
Own Heating Curve P1 | User defined heating curve point | 47026 | °C | s8 | 1 | 5 | 70 | 45 | R/W
Point offset outdoor temp. | Outdoor temperature point where the heat curve is offset | 47027 | °C | s8 | 1 | -40 | 30 | 0 | R/W
Point offset | Amount of offset at the point offset temperature | 47028 | °C | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S4 | Change of the offset of the heat curve when closing the external adjustment input | 47029 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S3 | Change of the offset of the heat curve when closing the external adjustment input | 47030 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S2 | Change of the offset of the heat curve when closing the external adjustment input | 47031 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S1 | Change of the offset of the heat curve when closing the external adjustment input | 47032 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment with room sensor S4 | Room temperature setting when closing the external adjustment input | 47033 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S3 | Room temperature setting when closing the external adjustment input | 47034 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S2 | Room temperature setting when closing the external adjustment input | 47035 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S1 | Room temperature setting when closing the external adjustment input | 47036 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Hot water mode | 0=Economy 1=Normal 2=Luxury | 47041 |  | s8 | 1 | 0 | 2 | 1 | R/W
Start temperature HW Luxury | Start temperature for heating water | 47043 | °C | s16 | 10 | 50 | 700 | 520 | R/W
Start temperature HW Normal | Start temperature for heating water | 47044 | °C | s16 | 10 | 50 | 700 | 490 | R/W
Start temperature HW Economy | Start temperature for heating water | 47045 | °C | s16 | 10 | 50 | 700 | 450 | R/W
Stop temperature Periodic HW | Temperature where hot water generation will stop | 47046 | °C | s16 | 10 | 550 | 700 | 550 | R/W
Stop temperature HW Luxury | Temperature where hot water generation will stop | 47047 | °C | s16 | 10 | 50 | 700 | 580 | R/W
Stop temperature HW Normal | Temperature where hot water generation will stop | 47048 | °C | s16 | 10 | 50 | 700 | 550 | R/W
Stop temperature HW Economy | Temperature where hot water generation will stop | 47049 | °C | s16 | 10 | 50 | 700 | 510 | R/W
Periodic HW | Activates the periodic hot water generation | 47050 |  | s8 | 1 | 0 | 1 | 1 | R/W
Periodic HW Interval | Interval between Periodic hot water sessions | 47051 | days | s8 | 1 | 1 | 90 | 14 | R/W
Run time HWC | Run time for the hot water circulation system | 47054 | min | s8 | 1 | 1 | 60 | 60 | R/W
Still time HWC | Still time for the hot water circulation system | 47055 | min | s8 | 1 | 0 | 60 | 0 | R/W
GMz | Compressor frequency regulator GMz | 47099 |  | u8 | 1 | 0 | 0 | 0 | R/W
Comp freq reg P | Compressor frequency regulator P | 47101 |  | u8 | 1 | 0 | 0 | 0 | R/W
Language | Display language in the heat pump 0=English 1=Svenska 2=Deutsch 3=Francais 4=Espanol 5=Suomi 6=Lietuviu 7=Cesky 8=Polski 9=Nederlands 10=Norsk 11=Dansk 12=Eesti 13=Latviesu 16=Magyar | 47131 |  | s8 | 1 | 0 | 20 | 0 | R/W
Period HW |  | 47134 | min | u8 | 1 | 0 | 180 | 60 | R/W
Period Heat |  | 47135 | min | u8 | 1 | 0 | 180 | 0 | R/W
Period Pool |  | 47136 | min | u8 | 1 | 0 | 180 | 0 | R/W
Operational mode heat medium pump | 10=Intermittent 20=Continous 30=Economy 40=Auto | 47138 |  | u8 | 1 | 10 | 40 | 40 | R/W
Operational mode brine medium pump | 10=Intermittent 20=Continuous 30=Economy 40=Auto | 47139 |  | u8 | 1 | 10 | 30 | 10 | R/W
DM start heating | The value the degree minutes needed to be reached for the pump to start heating | 47206 |  | s16 | 1 | -1000 | -30 | -60 | R/W
DM start cooling | The value the degree minutes needed to be reached for the pump to start cooling | 47207 |  | s16 | 1 | 0 | 0 | 0 | R/W
DM start add. | The value the degree minutes needed to be reached for the pump to start electric addition | 47208 |  | s16 | 1 | 0 | 0 | 0 | R/W
DM between add. steps | The number of degree minutes between start of each electric addition step | 47209 |  | s16 | 1 | 0 | 0 | 0 | R/W
DM start add. with shunt |  | 47210 |  | s16 | 1 | -2000 | -30 | -400 | R/W
Max int add. power |  | 47212 | kW | s16 | 100 | 0 | 4500 | 600 | R/W
Fuse | Size of the fuse that the HP is connected to | 47214 | A | u8 | 1 | 1 | 200 | 16 | R/W
Exhaust Fan speed 4 |  | 47261 | % | u8 | 1 | 0 | 100 | 100 | R/W
Exhaust Fan speed 3 |  | 47262 | % | u8 | 1 | 0 | 100 | 80 | R/W
Exhaust Fan speed 2 |  | 47263 | % | u8 | 1 | 0 | 100 | 30 | R/W
Exhaust Fan speed 1 |  | 47264 | % | u8 | 1 | 0 | 100 | 0 | R/W
Exhaust Fan speed normal |  | 47265 | % | u8 | 1 | 0 | 100 | 65 | R/W
Fan return time 4 | Time from a changed fan speed until it returns to normal speed | 47271 | h | u8 | 1 | 1 | 99 | 4 | R/W
Fan return time 3 | Time from a changed fan speed until it returns to normal speed | 47272 | h | u8 | 1 | 1 | 99 | 4 | R/W
Fan return time 2 | Time from a changed fan speed until it returns to normal speed | 47273 | h | u8 | 1 | 1 | 99 | 4 | R/W
Fan return time 1 | Time from a changed fan speed until it returns to normal speed | 47274 | h | u8 | 1 | 1 | 99 | 4 | R/W
Filter Reminder period | Time between the reminder of filter replacement/cleaning. | 47275 | Months | u8 | 1 | 1 | 24 | 3 | R/W
Floor drying | 0=Off 1=On | 47276 |  | u8 | 1 | 0 | 1 | 0 | R/W
Floor drying period 7 | Days each period is active | 47277 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 6 | Days each period is active | 47278 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 5 | Days each period is active | 47279 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 4 | Days each period is active | 47280 | days | u8 | 1 | 0 | 30 | 3 | R/W
Floor drying period 3 | Days each period is active | 47281 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 2 | Days each period is active | 47282 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 1 | Days each period is active | 47283 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying temp. 7 | Supply temperature each period | 47284 | °C | u8 | 1 | 15 | 70 | 20 | R/W
Floor drying temp. 6 | Supply temperature each period | 47285 | °C | u8 | 1 | 15 | 70 | 30 | R/W
Floor drying temp. 5 | Supply temperature each period | 47286 | °C | u8 | 1 | 15 | 70 | 40 | R/W
Floor drying temp. 4 | Supply temperature each period | 47287 | °C | u8 | 1 | 15 | 70 | 45 | R/W
Floor drying temp. 3 | Supply temperature each period | 47288 | °C | u8 | 1 | 15 | 70 | 40 | R/W
Floor drying temp. 2 | Supply temperature each period | 47289 | °C | u8 | 1 | 15 | 70 | 30 | R/W
Floor drying temp. 1 | Supply temperature each period | 47290 | °C | u8 | 1 | 15 | 70 | 20 | R/W
Climate system 2 accessory | Activates the climate system 2 accessory 0=Off 1=On | 47302 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 3 accessory | Activates the climate system 3 accessory 0=Off 1=On | 47303 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 4 accessory | Activates the climate system 4 accessory 0=Off 1=On | 47304 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 4 mixing valve amp. | Mixing valve amplification for extra climate systems | 47305 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 3 mixing valve amp. | Mixing valve amplification for extra climate systems | 47306 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 2 mixing valve amp. | Mixing valve amplification for extra climate systems | 47307 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 4 shunt wait | Wait time between changes of the shunt in extra climate systems | 47308 | secs | s16 | 10 | 10 | 300 | 30 | R/W
Climate system 3 shunt wait | Wait time between changes of the shunt in extra climate systems | 47309 | secs | s16 | 10 | 10 | 300 | 30 | R/W
Climate system 2 shunt wait | Wait time between changes of the shunt in extra climate systems | 47310 | secs | s16 | 10 | 10 | 300 | 30 | R/W
FLM pump | Operating mode for the FLM pump 0=Off 1=On | 47312 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM defrost | Minimum time between defrost in FLM | 47313 | hrs | u8 | 1 | 1 | 30 | 10 | R/W
Shunt controlled add. accessory | Activates the shunt controlled addition accessory 0=Off 1=On | 47317 |  | u8 | 1 | 0 | 1 | 0 | R/W
Shunt controlled add. min. temp. |  | 47318 | °C | s8 | 1 | 5 | 90 | 55 | R/W
Shunt controlled add. min. runtime |  | 47319 | hrs | u8 | 1 | 0 | 48 | 12 | R/W
Shunt controlled add. mixing valve amp. | Mixing valve amplification for shunt controlled add. | 47320 |  | s8 | 10 | 1 | 100 | 10 | R/W
Shunt controlled add. mixing valve wait | Wait time between changes of the shunt in shunt controlled add. | 47321 | secs | s16 | 1 | 10 | 300 | 30 | R/W
Step controlled add. accessory | Activates the step controlled addition accessory 0=Off 1=On | 47322 |  | u8 | 1 | 0 | 1 | 0 | R/W
Step controlled add. start DM | DM where the first step of step controlled add. starts | 47323 |  | s16 | 1 | -2000 | -30 | -400 | R/W
Step controlled add. diff. DM | Difference in DM of each step in the step controlled add. | 47324 |  | s16 | 1 | 0 | 1000 | 100 | R/W
Step controlled add. mode | Binary or linear stepping method. 0=Linear 1=Binary | 47326 |  | u8 | 1 | 0 | 1 | 0 | R/W
Ground water pump accessory | Ground water pump using AXC40 0=Off 1=On | 47327 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling 2-pipe accessory | Activates the 2-pipe cooling accessory 0=Off 1=On | 47329 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling 4-pipe accessory | Activates the 4-pipe cooling accessory 0=Off 1=On | 47330 |  | u8 | 1 | 0 | 1 | 0 | R/W
Time betw. switch heat/cool | Time between switching from heating to cooling or vice versa. | 47335 | h | s8 | 1 | 0 | 48 | 2 | R/W
Heat at room under temp. | This value indicates how many degrees under set room temp heating will be allowed | 47336 | °C | s8 | 10 | 5 | 100 | 10 | R/W
Cool at room over temp. | This value indicates how many degrees over set room temp cooling will be allowed | 47337 | °C | s8 | 10 | 5 | 100 | 30 | R/W
Cooling mix. valve amp. | Mixing valve amplification for the cooling valve | 47338 |  | s8 | 10 | 1 | 100 | 10 | R/W
Cooling mix. valve step delay |  | 47339 | s | s16 | 1 | 10 | 300 | 30 | R/W
Cooling with room sensor | Enables use of room sensor together with cooling 0=Off 1=On | 47340 |  | u8 | 10 | 0 | 18 | 0 | R/W
HPAC accessory | Activates the HPAC accessory | 47341 |  | u8 | 1 | 0 | 1 | 0 | R/W
Start Passive Cooling DM | Value the degree minutes have to reach to start passive cooling | 47342 |  | s16 | 1 | 10 | 500 | 30 | R/W
Start Active Cooling DM | Value the degree minutes have to reach to start active cooling | 47343 |  | s16 | 1 | 10 | 300 | 90 | R/W
SMS40 accessory | Activates the SMS40 accessory | 47352 |  | u8 | 1 | 0 | 1 | 0 | R/W
RMU System 1 | Activates the RMU accessory for system 1 | 47365 |  | u8 | 1 | 0 | 1 | 0 | R/W
RMU System 2 | Activates the RMU accessory for system 2 | 47366 |  | u8 | 1 | 0 | 1 | 0 | R/W
RMU System 3 | Activates the RMU accessory for system 3 | 47367 |  | u8 | 1 | 0 | 1 | 0 | R/W
RMU System 4 | Activates the RMU accessory for system 4 | 47368 |  | u8 | 1 | 0 | 1 | 0 | R/W
Allow Additive Heating | Whether to allow additive heating (only valid for operational mode Manual) | 47370 |  | u8 | 1 | 0 | 1 | 1 | R/W
Allow Heating | Whether to allow heating (only valid for operational mode Manual or Add. heat only) | 47371 |  | u8 | 1 | 0 | 1 | 1 | R/W
Allow Cooling | Whether to allow cooling (only valid for operational mode Manual or Add. heat only) | 47372 |  | u8 | 1 | 0 | 1 | 1 | R/W
Start Temperature Cooling | 0=Off 1=On | 47374 | °C | s16 | 10 | -200 | 400 | 250 | R/W
Start Temperature Heating |  | 47375 | °C | s16 | 10 | -200 | 400 | 170 | R/W
Start Temperature Additive | 1=DD/MM/YY 2=YYMMDD | 47376 | °C | s16 | 10 | -250 | 400 | 150 | R/W
Outdoor Filter Time | 12=12 Hours 24=24 Hours | 47377 | h | u8 | 1 | 0 | 48 | 24 | R/W
Max diff. comp. |  | 47378 | °C | s16 | 10 | 10 | 250 | 100 | R/W
Max diff. add. |  | 47379 | °C | s16 | 10 | 10 | 240 | 70 | R/W
Low brine out autoreset | 0=Off 1=On | 47380 |  | u8 | 1 | 0 | 1 | 0 | R/W
Low brine out temp. |  | 47381 | °C | s16 | 10 | -120 | 150 | -80 | R/W
High brine in | Activates the High brine in temperature alarm. 0=Off 1=On | 47382 |  | u8 | 1 | 0 | 1 | 0 | R/W
High brine in temp. | The brine in temperature that triggers the high brine in temperature alarm (if active). | 47383 | °C | s16 | 10 | 100 | 300 | 200 | R/W
Date format | 1=DD-MM-YY 2=YY-MM-DD | 47384 |  | u8 | 1 | 1 | 2 | 1 | R/W
Time format | 12=12 hours 24=24 Hours | 47385 |  | u8 | 1 | 12 | 24 | 24 | R/W
HW production | Activates hot water production where applicable 0=Off 1=On | 47387 |  | u8 | 1 | 0 | 1 | 0 | R/W
Alarm lower room temp. | Lowers the room temperature during red light alarms to notify the occupants of the building that something is the matter 0=Off 1=On | 47388 |  | u8 | 1 | 0 | 1 | 0 | R/W
Alarm lower HW temp. | Lowers the hot water temperature during red light alarms to notify the occupants of the building that something is the matter 0=Off 1=On | 47389 |  | u8 | 1 | 0 | 1 | 1 | R/W
Use room sensor S4 | When activated the system uses the room sensor 0=Off 1=On | 47391 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S3 | When activated the system uses the room sensor 0=Off 1=On | 47392 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S2 | When activated the system uses the room sensor 0=Off 1=On | 47393 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S1 | When activated the system uses the room sensor 0=Off 1=On | 47394 |  | u8 | 1 | 0 | 1 | 0 | R/W
Room sensor setpoint S4 | Sets the room temperature setpoint for the system | 47395 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S3 | Sets the room temperature setpoint for the system | 47396 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S2 | Sets the room temperature setpoint for the system | 47397 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S1 | Sets the room temperature setpoint for the system | 47398 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor factor S4 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47399 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S3 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47400 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S2 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47401 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S1 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47402 |  | u8 | 10 | 0 | 60 | 20 | R/W
Speed circ.pump HW |  | 47413 | % | u8 | 1 | 1 | 100 | 70 | R/W
Speed circ.pump Heat |  | 47414 | % | u8 | 1 | 1 | 100 | 70 | R/W
Speed circ.pump Pool |  | 47415 | % | u8 | 1 | 1 | 100 | 70 | R/W
Speed circ.pump Economy |  | 47416 | % | u8 | 1 | 1 | 100 | 30 | R/W
Speed circ.pump Cooling |  | 47417 | % | u8 | 1 | 1 | 100 | 70 | R/W
Speed brine pump |  | 47418 | % | u8 | 1 | 1 | 100 | 100 | R/W
Heat curve S8 | Heat curve to use see manual for the different curves. | 47525 |  | s8 | 1 | 0 | 15 | 9 | R/W
Night cooling | If the fan should have a higher speed when there is a high room temp and a low outdoor temp. 0=Off 1=On | 47537 |  | u8 | 1 | 0 | 1 | 0 | R/W
Start room temp. night cooling |  | 47538 | °C | u8 | 1 | 20 | 30 | 25 | R/W
Night Cooling Min. diff. | Minimum difference between room temp and outdoor temp to start night cooling | 47539 | °C | u8 | 1 | 3 | 10 | 6 | R/W
Heat curve S7 | Heat curve to use see manual for the different curves. | 47567 |  | s8 | 1 | 0 | 15 | 9 | R/W
Operational mode | The operational mode of the heat pump 0=Auto 1=Manual 2=Add. heat only | 47570 |  | u8 | 1 | 0 | 0 | 0 | R/W
FLM 2 speed 4 |  | 48053 | % | u8 | 1 | 0 | 100 | 100 | R/W
FLM 2 speed 3 |  | 48054 | % | u8 | 1 | 0 | 100 | 80 | R/W
FLM 2 speed 2 |  | 48055 | % | u8 | 1 | 0 | 100 | 30 | R/W
FLM 2 speed 1 |  | 48056 | % | u8 | 1 | 0 | 100 | 0 | R/W
FLM 2 speed normal |  | 48057 | % | u8 | 1 | 0 | 100 | 65 | R/W
FLM 3 speed 4 |  | 48058 | % | u8 | 1 | 0 | 100 | 100 | R/W
FLM 3 speed 3 |  | 48059 | % | u8 | 1 | 0 | 100 | 80 | R/W
FLM 3 speed 2 |  | 48060 | % | u8 | 1 | 0 | 100 | 30 | R/W
FLM 3 speed 1 |  | 48061 | % | u8 | 1 | 0 | 100 | 0 | R/W
FLM 3 speed normal |  | 48062 | % | u8 | 1 | 0 | 100 | 65 | R/W
FLM 4 speed 4 |  | 48063 | % | u8 | 1 | 0 | 100 | 100 | R/W
FLM 4 speed 3 |  | 48064 | % | u8 | 1 | 0 | 100 | 80 | R/W
FLM 4 speed 2 |  | 48065 | % | u8 | 1 | 0 | 100 | 30 | R/W
FLM 4 speed 1 |  | 48066 | % | u8 | 1 | 0 | 100 | 0 | R/W
FLM 4 speed normal |  | 48067 | % | u8 | 1 | 0 | 100 | 65 | R/W
FLM 4 accessory | Activates the FLM 4 accessory | 48068 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM 3 accessory | Activates the FLM 3 accessory | 48069 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM 2 accessory | Activates the FLM 2 accessory | 48070 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM 1 accessory | Activates the FLM 1 accessory | 48071 |  | u8 | 1 | 0 | 1 | 0 | R/W
DM diff start add. | The value below the last compressor step the degree minutes needed to be reached for the pump to start electric addition | 48072 |  | s16 | 1 | 0 | 0 | 0 | R/W
FLM cooling | FLM cooling activated | 48073 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cool/Heat Sensor Set Point | Set point for change between cooling and heating when using the cool/heat sensor | 48074 |  | s16 | 10 | 50 | 400 | 210 | R/W
Pool 2 accessory | Activate the pool 2 accessory | 48087 |  | u8 | 1 | 0 | 1 | 0 | R/W
Pool 1 accessory | Activates the pool 1 accessory | 48088 |  | u8 | 1 | 0 | 1 | 0 | R/W
Pool 2 start temp. | The Temperature below which the pool heating should start | 48089 | °C | s16 | 10 | 50 | 800 | 220 | R/W
Pool 1 start temp. | The Temperature below which the pool heating should start | 48090 | °C | s16 | 10 | 50 | 800 | 220 | R/W
Pool 2 stop temp. | The Temperature at which the pool heating will stop | 48091 | °C | s16 | 10 | 50 | 800 | 240 | R/W
Pool 1 stop temp. | The Temperature at which the pool heating will stop | 48092 | °C | s16 | 10 | 50 | 800 | 240 | R/W
Pool 2 Activated | Activates pool heating | 48093 |  | u8 | 1 | 0 | 1 | 1 | R/W
Pool 1 Activated | Activates pool heating | 48094 |  | u8 | 1 | 0 | 1 | 1 | R/W
Period Pool 2 |  | 48133 | min | u8 | 1 | 0 | 180 | 30 | R/W
Min cooling supply temp S4 | Minimum allowed supply temperature during cooling | 48174 | °C | s8 | 1 | -5 | 30 | 18 | R/W
Min cooling supply temp S3 | Minimum allowed supply temperature during cooling | 48175 | °C | s8 | 1 | -5 | 30 | 18 | R/W
Min cooling supply temp S2 | Minimum allowed supply temperature during cooling | 48176 | °C | s8 | 1 | -5 | 30 | 18 | R/W
Min cooling supply temp S1 | Minimum allowed supply temperature during cooling | 48177 | °C | s8 | 1 | -5 | 30 | 18 | R/W
Own Cooling Curve P3 | User defined cooling curve point | 48181 | °C | s8 | 1 | -5 | 40 | 20 | R/W
Own Cooling Curve P5 | User defined cooling curve point | 48185 | °C | s8 | 1 | -5 | 40 | 20 | R/W
Cooling use mix. valve S4 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system | 48186 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valve S3 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system | 48187 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valve S2 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system | 48188 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valve S1 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system | 48189 |  | u8 | 1 | 0 | 0 | 0 | R/W
Heatdump mix. valve delay | Mixing valve step delay for the heatdump valve | 48190 | s | s16 | 1 | 10 | 500 | 30 | R/W
Heatdump mix. valve amp. | Mixing valve amplification for the heatdump valve | 48191 |  | s8 | 10 | 1 | 100 | 10 | R/W
Cooldump mix. valve delay | Mixing valve step delay for the cooldump valve for the ACS-system | 48192 | s | s16 | 1 | 10 | 500 | 30 | R/W
Cooldump mix. valve amp. | Mixing valve amplification for the cooldump valve for the ACS-system | 48193 |  | s8 | 10 | 1 | 100 | 10 | R/W
ACS accessory | Activate the ACS accessory | 48194 |  | u8 | 1 | 0 | 1 | 0 | R/W
ACS heat dump 24h-function |  | 48195 |  | u8 | 1 | 0 | 1 | 0 | R/W
ACS closingtime for cool dump |  | 48197 | s | u8 | 1 | 0 | 100 | 0 | R/W
SG Ready heating | Sets whether or not SG Ready should affect heating | 48282 |  | u8 | 1 | 0 | 1 | 1 | R/W
SG Ready cooling | Sets whether or not SG Ready should affect cooling | 48283 |  | u8 | 1 | 0 | 1 | 1 | R/W
SG Ready hot water | Sets whether or not SG Ready should affect hot water | 48284 |  | u8 | 1 | 0 | 1 | 1 | R/W
SG Ready pool | Sets whether or not SG Ready should affect pool | 48285 |  | u8 | 1 | 0 | 1 | 1 | R/W
Pool 2 Cpr Percentage |  | 48286 | % | u8 | 1 | 1 | 100 | 1 | R/W
Pool 1 Cpr Percentage |  | 48287 | % | u8 | 1 | 1 | 100 | 1 | R/W
Cool Cpr Percentage |  | 48288 | % | u8 | 1 | 1 | 100 | 1 | R/W
Max speed circ.pump Heat |  | 48458 | % | u8 | 1 | 50 | 100 | 100 | R/W
Speed brine pump passive cooling |  | 48459 | % | u8 | 1 | 0 | 100 | 75 | R/W
Speed circ.pump Cooling |  | 48487 | % | u8 | 1 | 1 | 100 | 70 | R/W
Heat curve S6 | Heat curve to use see manual for the different curves. | 48488 |  | s8 | 1 | 0 | 15 | 9 | R/W
Heat curve S5 | Heat curve to use see manual for the different curves. | 48489 |  | s8 | 1 | 0 | 15 | 9 | R/W
Offset S8 | Offset of the heat curve | 48491 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S7 | Offset of the heat curve | 48492 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S6 | Offset of the heat curve | 48493 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S5 | Offset of the heat curve | 48494 |  | s8 | 1 | -10 | 10 | 0 | R/W
Min Supply System 8 |  | 48495 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 7 |  | 48496 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 6 |  | 48497 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 5 |  | 48498 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Max Supply System 8 |  | 48499 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 7 |  | 48500 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 6 |  | 48501 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 5 |  | 48502 | °C | s16 | 10 | 50 | 700 | 600 | R/W
External adjustment S8 | Change of the offset of the heat curve when closing the external adjustment input | 48503 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S7 | Change of the offset of the heat curve when closing the external adjustment input | 48504 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S6 | Change of the offset of the heat curve when closing the external adjustment input | 48505 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S5 | Change of the offset of the heat curve when closing the external adjustment input | 48506 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment with room sensor S8 | Room temperature setting when closing the external adjustment input | 48507 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S7 | Room temperature setting when closing the external adjustment input | 48508 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S6 | Room temperature setting when closing the external adjustment input | 48509 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S5 | Room temperature setting when closing the external adjustment input | 48510 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Climate system 5 accessory | Activates the climate system 5 accessory | 48569 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 6 accessory | Activates the climate system 6 accessory | 48570 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 7 accessory | Activates the climate system 7 accessory | 48571 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 8 accessory | Activates the climate system 8 accessory | 48572 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 8 mixing valve amp. | Mixing valve amplification for extra climate systems | 48573 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 7 mixing valve amp. | Mixing valve amplification for extra climate systems | 48574 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 6 mixing valve amp. | Mixing valve amplification for extra climate systems | 48575 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 5 mixing valve amp. | Mixing valve amplification for extra climate systems | 48576 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 8 shunt wait | Wait time between changes of the shunt in extra climate systems | 48577 | secs | s16 | 10 | 10 | 300 | 30 | R/W
Climate system 7 shunt wait | Wait time between changes of the shunt in extra climate systems | 48578 | secs | s16 | 10 | 10 | 300 | 30 | R/W
Climate system 6 shunt wait | Wait time between changes of the shunt in extra climate systems | 48579 | secs | s16 | 10 | 10 | 300 | 30 | R/W
Climate system 5 shunt wait | Wait time between changes of the shunt in extra climate systems | 48580 | secs | s16 | 10 | 10 | 300 | 30 | R/W
Min cooling supply temp S8 | Minimum allowed supply temperature during cooling | 48581 | °C | s8 | 1 | -5 | 30 | 18 | R/W
Min cooling supply temp S7 | Minimum allowed supply temperature during cooling | 48582 | °C | s8 | 1 | -5 | 30 | 18 | R/W
Min cooling supply temp S6 | Minimum allowed supply temperature during cooling | 48583 | °C | s8 | 1 | -5 | 30 | 18 | R/W
Min cooling supply temp S5 | Minimum allowed supply temperature during cooling | 48584 | °C | s8 | 1 | -5 | 30 | 18 | R/W
Cooling use mix. valve S8 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system | 48593 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valve S7 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system | 48594 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valve S6 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system | 48595 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valve S5 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system | 48596 |  | u8 | 1 | 0 | 1 | 0 | R/W
Heating use mix. valve S8 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. | 48597 |  | u8 | 1 | 0 | 1 | 1 | R/W
Heating use mix. valve S7 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. | 48598 |  | u8 | 1 | 0 | 1 | 1 | R/W
Heating use mix. valve S6 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. | 48599 |  | u8 | 1 | 0 | 1 | 1 | R/W
Heating use mix. valve S5 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. | 48600 |  | u8 | 1 | 0 | 1 | 1 | R/W
Heating use mix. valve S4 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. | 48601 |  | u8 | 1 | 0 | 1 | 1 | R/W
Heating use mix. valve S3 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. | 48602 |  | u8 | 1 | 0 | 1 | 1 | R/W
Heating use mix. valve S2 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. | 48603 |  | u8 | 1 | 0 | 1 | 1 | R/W
Heating use mix. valve S1 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. | 48604 |  | u8 | 1 | 0 | 1 | 1 | R/W
Cut off frequency activated 2 | Cut off frequency activeted | 48659 |  | s8 | 1 | 0 | 1 | 0 | R/W
Cut off frequency activated 1 | Cut off frequency activeted | 48660 |  | s8 | 1 | 0 | 1 | 0 | R/W
Cut off frequency start 2 | Cut off frequency start | 48661 | Hz | u8 | 1 | 17 | 115 | 17 | R/W
Cut off frequency start 1 | Cut off frequency start | 48662 | Hz | u8 | 1 | 17 | 115 | 17 | R/W
Cut off frequency stop 2 | Cut off frequency stop | 48663 | Hz | u8 | 1 | 22 | 120 | 22 | R/W
Cut off frequency stop 1 | Cut off frequency stop | 48664 | Hz | u8 | 1 | 22 | 120 | 22 | R/W
Use room sensor S8 | When activated the system uses the room sensor | 48675 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S7 | When activated the system uses the room sensor | 48676 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S6 | When activated the system uses the room sensor | 48677 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S5 | When activated the system uses the room sensor | 48678 |  | u8 | 1 | 0 | 1 | 0 | R/W
Room sensor setpoint S8 | Sets the room temperature setpoint for the system | 48680 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S7 | Sets the room temperature setpoint for the system | 48681 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S6 | Sets the room temperature setpoint for the system | 48682 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S5 | Sets the room temperature setpoint for the system | 48683 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor factor S8 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 48685 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S7 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 48686 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S6 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 48687 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S5 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 48688 |  | u8 | 10 | 0 | 60 | 20 | R/W
Cool curve S8 | Cool curve to use see manual for the different curves. | 48724 |  | s8 | 1 | 0 | 9 | 0 | R/W
Cool curve S7 | Cool curve to use see manual for the different curves. | 48725 |  | s8 | 1 | 0 | 9 | 0 | R/W
Cool curve S6 | Cool curve to use see manual for the different curves. | 48726 |  | s8 | 1 | 0 | 9 | 0 | R/W
Cool curve S5 | Cool curve to use see manual for the different curves. | 48727 |  | s8 | 1 | 0 | 9 | 0 | R/W
Cool curve S4 | Cool curve to use see manual for the different curves. | 48728 |  | s8 | 1 | 0 | 9 | 0 | R/W
Cool curve S3 | Cool curve to use see manual for the different curves. | 48729 |  | s8 | 1 | 0 | 9 | 0 | R/W
Cool curve S2 | Cool curve to use see manual for the different curves. | 48730 |  | s8 | 1 | 0 | 9 | 0 | R/W
Cool curve S1 | Cool curve to use see manual for the different curves. | 48731 |  | s8 | 1 | 0 | 9 | 0 | R/W
Cool offset S8 | Offset of the cooling curve | 48732 |  | s8 | 1 | -10 | 10 | 0 | R/W
Cool offset S7 | Offset of the cooling curve | 48733 |  | s8 | 1 | -10 | 10 | 0 | R/W
Cool offset S6 | Offset of the cooling curve | 48734 |  | s8 | 1 | -10 | 10 | 0 | R/W
Cool offset S5 | Offset of the cooling curve | 48735 |  | s8 | 1 | -10 | 10 | 0 | R/W
Cool offset S4 | Offset of the cooling curve | 48736 |  | s8 | 1 | -10 | 10 | 0 | R/W
Cool offset S3 | Offset of the cooling curve | 48737 |  | s8 | 1 | -10 | 10 | 0 | R/W
Cool offset S2 | Offset of the cooling curve | 48738 |  | s8 | 1 | -10 | 10 | 0 | R/W
Cool offset S1 | Offset of the cooling curve | 48739 |  | s8 | 1 | -10 | 10 | 0 | R/W
Own Cooling Curve P4 | User defined cooling curve point | 48740 | °C | s8 | 1 | -5 | 40 | 20 | R/W
Own Cooling Curve P2 | User defined cooling curve point | 48741 | °C | s8 | 1 | -5 | 40 | 20 | R/W
Own Cooling Curve P1 | User defined cooling curve point | 48742 | °C | s8 | 1 | -5 | 40 | 20 | R/W
Hot water high power mode |  | 48743 |  | s8 | 1 | 0 | 1 | 0 | R/W
Transformer ratio | Ratio of the current measurement transformers | 48755 |  | u16 | 1 | 300 | 3000 | 300 | R/W
Room sensor cool setpoint S8 | Sets the room temperature setpoint for the system in cooling mode | 48778 | °C | s16 | 10 | 50 | 350 | 250 | R/W
Room sensor cool setpoint S7 | Sets the room temperature setpoint for the system in cooling mode | 48779 | °C | s16 | 10 | 50 | 350 | 250 | R/W
Room sensor cool setpoint S6 | Sets the room temperature setpoint for the system in cooling mode | 48780 | °C | s16 | 10 | 50 | 350 | 250 | R/W
Room sensor cool setpoint S5 | Sets the room temperature setpoint for the system in cooling mode | 48781 | °C | s16 | 10 | 50 | 350 | 250 | R/W
Room sensor cool setpoint S4 | Sets the room temperature setpoint for the system in cooling mode | 48782 | °C | s16 | 10 | 50 | 350 | 250 | R/W
Room sensor cool setpoint S3 | Sets the room temperature setpoint for the system in cooling mode | 48783 | °C | s16 | 10 | 50 | 350 | 250 | R/W
Room sensor cool setpoint S2 | Sets the room temperature setpoint for the system in cooling mode | 48784 | °C | s16 | 10 | 50 | 350 | 250 | R/W
Room sensor cool setpoint S1 | Sets the room temperature setpoint for the system in cooling mode | 48785 | °C | s16 | 10 | 50 | 350 | 250 | R/W
Room sensor cool factor S8 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. | 48786 |  | u8 | 10 | 0 | 60 | 10 | R/W
Room sensor cool factor S7 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. | 48787 |  | u8 | 10 | 0 | 60 | 10 | R/W
Room sensor cool factor S6 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. | 48788 |  | u8 | 10 | 0 | 60 | 10 | R/W
Room sensor cool factor S5 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. | 48789 |  | u8 | 10 | 0 | 60 | 10 | R/W
Room sensor cool factor S4 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. | 48790 |  | u8 | 10 | 0 | 60 | 10 | R/W
Room sensor cool factor S3 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. | 48791 |  | u8 | 10 | 0 | 60 | 10 | R/W
Room sensor cool factor S2 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. | 48792 |  | u8 | 10 | 0 | 60 | 10 | R/W
Room sensor cool factor S1 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. | 48793 |  | u8 | 10 | 0 | 60 | 10 | R/W
RH set value | RH set value | 48794 | % | s8 | 1 | 30 | 90 | 60 | R/W
HTS accessory | HTS accessory | 48808 |  | u8 | 1 | 0 | 1 | 0 | R/W
Prevent humidity S8 |  | 48810 |  | s8 | 1 | 0 | 1 | 0 | R/W
Prevent humidity S7 |  | 48811 |  | s8 | 1 | 0 | 1 | 0 | R/W
Prevent humidity S6 |  | 48812 |  | s8 | 1 | 0 | 1 | 0 | R/W
Prevent humidity S5 |  | 48813 |  | s8 | 1 | 0 | 1 | 0 | R/W
Prevent humidity S4 |  | 48814 |  | s8 | 1 | 0 | 1 | 0 | R/W
Prevent humidity S3 |  | 48815 |  | s8 | 1 | 0 | 1 | 0 | R/W
Prevent humidity S2 |  | 48816 |  | s8 | 1 | 0 | 1 | 0 | R/W
Prevent humidity S1 |  | 48817 |  | s8 | 1 | 0 | 1 | 0 | R/W
Limit humidity in room S8 | Limit humidity in room | 48819 |  | s8 | 1 | 0 | 1 | 1 | R/W
Limit humidity in room S7 | Limit humidity in room | 48820 |  | s8 | 1 | 0 | 1 | 1 | R/W
Limit humidity in room S6 | Limit humidity in room | 48821 |  | s8 | 1 | 0 | 1 | 1 | R/W
Limit humidity in room S5 | Limit humidity in room | 48822 |  | s8 | 1 | 0 | 1 | 1 | R/W
Limit humidity in room S4 | Limit humidity in room | 48823 |  | s8 | 1 | 0 | 1 | 1 | R/W
Limit humidity in room S3 | Limit humidity in room | 48824 |  | s8 | 1 | 0 | 1 | 1 | R/W
Limit humidity in room S2 | Limit humidity in room | 48825 |  | s8 | 1 | 0 | 1 | 1 | R/W
Limit humidity in room S1 | Limit humidity in room | 48826 |  | s8 | 1 | 0 | 1 | 1 | R/W
Speed brine pump active cooling |  | 48849 | % | u8 | 1 | 0 | 100 | 75 | R/W
Delta brine pump active cooling |  | 48850 | % | u8 | 1 | 2 | 10 | 5 | R/W
Waiting speed brine pump cooling |  | 48851 | % | u8 | 1 | 0 | 100 | 30 | R/W
Modbus40 Word Swap | If set; swapping the words in 32-bit variables when value requested via ''read holding register'' commando. | 48852 |  | u8 | 1 | 0 | 1 | 1 | R/W
Modbus40 Disable LOG.SET | If set; The system will ignore a possible existing LOG.SET at the USB stick | 48889 |  | u8 | 1 | 0 | 1 | 0 | R/W
Energy Meter X23 | Activates the external energy meter | 48910 |  | u8 | 1 | 0 | 1 | 0 | R/W
Energy Meter X22 | Activates the external energy meter | 48911 |  | u8 | 1 | 0 | 1 | 0 | R/W