## LOG.SET.txt
[NIBL | 20180730 | 8310]
Divisors |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 10 | 1 | 1 | 1 | 1 | 1 | 1
Date | Time | Outdoor temp | Calc. Supply | Supply temp | Return temp | Hot water load | Hot water top | Evaporator temp | Compressor temp | Addition temp | Exhaust air temp | Vented air temp | Outdoor Average | Current L1 [A] | Current L2 [A] | Current L3 [A] | Addition power[kW] | Acc.heating[kWh] | Acc.hot water[kWh] | PCA-Base | Prio | Alarm number | Comp.state | Comp.starts | Comp.time[h]
40004 | 10 | Outdoor temp | BT1 Outdoor Temperature
43009 | 10 | Calc. Supply | Calc. Supply S1
40008 | 10 | Supply temp | BT2 Supply temp S1
40012 | 10 | Return temp | EB100-EP14-BT3 Return temp
40014 | 10 | Hot water load | BT6 HW Load
40013 | 10 | Hot water top | BT7 HW Top
40020 | 10 | Evaporator temp | EB100-BT16 Evaporator temp
40023 | 10 | Compressor temp | EB100-BT18 Compressor temp.
40024 | 10 | Addition temp | EB100-BT19 Addition temp.
40025 | 10 | Exhaust air temp | BT20 Exhaust air temp. 1
40026 | 10 | Vented air temp | BT21 Vented air temp. 1
40067 | 10 | Outdoor Average | BT1 Average
40083 | 10 | Current L1 [A] | EB100-BE1 Current
40081 | 10 | Current L2 [A] | EB100-BE2 Current
40079 | 10 | Current L3 [A] | EB100-BE3 Current
43084 | 100 | Addition power[kW] | Int. el.add. Power
44300 | 10 | Acc.heating[kWh] | Heat Meter - Heat Cpr and Add EP14
44298 | 10 | Acc.hot water[kWh] | Heat Meter - HW Cpr and Add EP14
43514 | 1 | PCA-Base | EB100-EP14 PCA Base Relays
43086 | 1 | Prio | Prio
45001 | 1 | Alarm number | Alarm
43427 | 1 | Comp.state | Compressor State EP14
43416 | 1 | Comp.starts | Compressor starts EB100-EP14
43420 | 1 | Comp.time[h] | Tot. op.time compr. EB100-EP14

## NIBE_Modbus_params
ModbusManager 1.0.9
Database: 8310
| Title | Info | F370 | F470 | F750 | F730 | F1255 | F1245 | F1355 | F1345 | SMO20 | SMO40 | VVM225 | VVM310 | Unit | Size | Factor | Min | Max | Default | Mode
32260 | NIBE Inverter 216-state |  |  |  | 32260 | 32260 | 32260 | [8 empty] | u8 | 1 | 0 | 0 | 0 | R
40004 | BT1 Outdoor Temperature | Current outdoor temperature | 40004 | 40004 | 40004 | 40004 | 40004 | 40004 | 40004 | 40004 | 40004 | 40004 | 40004 | 40004 | °C | s16 | 10 | 0 | 0 | 0 | R
40005 | EP23-BT2 Supply temp S4 | Supply temperature for system 4 | 40005 | 40005 | 40005 | 40005 | 40005 | 40005 | 40005 | 40005 |  | 40005 | 40005 | 40005 | °C | s16 | 10 | 0 | 0 | 0 | R
40006 | EP22-BT2 Supply temp S3 | Supply temperature for system 3 | 40006 | 40006 | 40006 | 40006 | 40006 | 40006 | 40006 | 40006 |  | 40006 | 40006 | 40006 | °C | s16 | 10 | 0 | 0 | 0 | R
40007 | EP21-BT2 Supply temp S2 | Supply temperature for system 2 | 40007 | 40007 | 40007 | 40007 | 40007 | 40007 | 40007 | 40007 |  | 40007 | 40007 | 40007 | °C | s16 | 10 | 0 | 0 | 0 | R
40008 | BT2 Supply temp S1 | Supply temperature for system 1 | 40008 | 40008 | 40008 | 40008 | 40008 | 40008 | 40008 |  |  |  | 40008 | 40008 | °C | s16 | 10 | 0 | 0 | 0 | R
40011 | EB100-EP15-BT3 Return temp | [7 empty] | 40011 | 40011 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40012 | EB100-EP14-BT3 Return temp | Return temperature | 40012 | 40012 | 40012 | 40012 | 40012 | 40012 | 40012 | 40012 | 40012 | 40012 | 40012 | 40012 | °C | s16 | 10 | 0 | 0 | 0 | R
40013 | BT7 HW Top | Hot water top temperature, BT7 | 40013 | 40013 | 40013 | 40013 | 40013 | 40013 | 40013 | 40013 | 40013 | 40013 | 40013 | 40013 | °C | s16 | 10 | 0 | 0 | 0 | R
40014 | BT6 HW Load | Hot water load temperature, BT6 | 40014 | 40014 | 40014 | 40014 | 40014 | 40014 | 40014 | 40014 | 40014 | 40014 | 40014 | 40014 | °C | s16 | 10 | 0 | 0 | 0 | R
40015 | EB100-EP14-BT10 Brine In Temp | Brine in temperature, BT10 |  |  |  |  | 40015 | 40015 | 40015 | 40015 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40016 | EB100-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 |  |  |  |  | 40016 | 40016 | 40016 | 40016 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40017 | EB100-EP14-BT12 Condensor Out | Condensor out temperature, BT12 |  |  | 40017 | 40017 | 40017 | 40017 | 40017 | 40017 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40018 | EB100-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 |  |  | 40018 | 40018 | 40018 | 40018 | 40018 | 40018 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40019 | EB100-EP14-BT15 Liquid Line | Liquid line temperature, BT15 |  |  | 40019 | 40019 | 40019 | 40019 | 40019 | 40019 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40020 | EB100-BT16 Evaporator temp |  | 40020 | 40020 | 40020 | 40020 | [8 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40022 | EB100-EP14-BT17 Suction | Suction temperature, BT17 | 40022 | 40022 | 40022 | 40022 | 40022 | 40022 | 40022 | 40022 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40023 | EB100-BT18 Compressor temp. | Valid only for F3/470 | 40023 | 40023 | [10 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40024 | EB100-BT19 Addition temp. | Valid only for F3/470 | 40024 | 40024 | [10 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40025 | BT20 Exhaust air temp. 1 |  | 40025 | 40025 | 40025 | 40025 | 40025 | 40025 | 40025 | 40025 |  | 40025 | 40025 | 40025 | °C | s16 | 10 | 0 | 0 | 0 | R
40026 | BT21 Vented air temp. 1 |  | 40026 | 40026 | 40026 | 40026 | 40026 | 40026 | 40026 | 40026 |  | 40026 | 40026 | 40026 | °C | s16 | 10 | 0 | 0 | 0 | R
40028 | AZ1-BT26 Temp Collector in FLM 1 | Connected to the FLM module |  |  |  |  | 40028 | 40028 | 40028 | 40028 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40029 | AZ1-BT27 Temp Collector out FLM 1 | Connected to the FLM module |  |  |  |  | 40029 | 40029 | 40029 | 40029 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40030 | EP23-BT50 Room Temp S4 |  | 40030 | 40030 | 40030 | 40030 | 40030 | 40030 | 40030 | 40030 |  | 40030 | 40030 | 40030 | °C | s16 | 10 | 0 | 0 | 0 | R
40031 | EP22-BT50 Room Temp S3 |  | 40031 | 40031 | 40031 | 40031 | 40031 | 40031 | 40031 | 40031 |  | 40031 | 40031 | 40031 | °C | s16 | 10 | 0 | 0 | 0 | R
40032 | EP21-BT50 Room Temp S2 |  | 40032 | 40032 | 40032 | 40032 | 40032 | 40032 | 40032 | 40032 |  | 40032 | 40032 | 40032 | °C | s16 | 10 | 0 | 0 | 0 | R
40033 | BT50 Room Temp S1 |  | 40033 | 40033 | 40033 | 40033 | 40033 | 40033 | 40033 | 40033 | 40033 | 40033 | 40033 | 40033 | °C | s16 | 10 | 0 | 0 | 0 | R
40042 | CL11-BT51 Pool 1 Temp | Pool temperature for Pool 1, BT51 |  |  |  |  | 40042 | 40042 | 40042 | 40042 |  | 40042 | 40042 | 40042 | °C | s16 | 10 | 0 | 0 | 0 | R
40043 | BT53 Solar Panel Temp | Used in Solar and AHPS Docking accessories | 40043 | 40043 | 40043 | 40043 | 40043 | 40043 | 40043 | 40043 |  | 40043 |  | 40043 | °C | s16 | 10 | 0 | 0 | 0 | R
40044 | BT54 Solar Load Temp | Used in Solar and AHPS Docking accessories | 40044 | 40044 | 40044 | 40044 | 40044 | 40044 | 40044 | 40044 |  | 40044 |  | 40044 | °C | s16 | 10 | 0 | 0 | 0 | R
40045 | EQ1-BT64 Cool Supply Temp | Cool supply temperature, BT64 |  |  |  |  | 40045 | 40045 | 40045 | 40045 | 40045 | 40045 | 40045 | 40045 | °C | s16 | 10 | 0 | 0 | 0 | R
40046 | EQ1-BT65 Cool Return Temp | Cool return temperature, BT65 |  |  |  |  | 40046 | 40046 | 40046 | 40046 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40047 | EB100-BT61 Supply Radiator Temp |  |  |  | 40047 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40048 | EB100-BT62 Return Radiator Temp |  |  |  | 40048 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40050 | EB100-BS1 Air flow |  |  |  | 40050 | 40050 | [9 empty] | s16 | 10 | 0 | 0 | 0 | R
40051 | EB100-BS1 Air flow unfiltered | Unfiltered air flow value |  |  | 40051 | 40051 | [9 empty] | s16 | 100 | 0 | 0 | 0 | R
40054 | EB100-FD1 Temperature limiter |  | 40054 | 40054 | 40054 | 40054 | 40054 | 40054 | 40054 | 40054 | 40054 | 40054 | 40054 | 40054 |  | s16 | 1 | 0 | 0 | 0 | R
40067 | BT1 Average | EB100-BT1 Outdoor temperature average | 40067 | 40067 | 40067 | 40067 | 40067 | 40067 | 40067 | 40067 | 40067 | 40067 | 40067 | 40067 | °C | s16 | 10 | 0 | 0 | 0 | R
40070 | EM1-BT52 Boiler Temperature | Boiler temperature, BT52 |  |  |  |  | 40070 | 40070 | 40070 | 40070 |  | 40070 | 40070 | 40070 | °C | s16 | 10 | 0 | 0 | 0 | R
40071 | BT25 Ext. Supply | External supply temperature, BT25 | 40071 | 40071 | 40071 | 40071 | 40071 | 40071 | 40071 | 40071 | 40071 | 40071 | 40071 |  | °C | s16 | 10 | 0 | 0 | 0 | R
40072 | BF1 EP14 Flow | Current flow EP14¦Current flow EP15 |  |  | 40072 | 40072 | 40072 | 40072 | 40072 | 40072 |  | 40072 | 40072 | 40072 | l/m | s16 | 10 | 0 | 0 | 0 | R
40074 | EB100-FR1 Anode Status |  | 40074 | 40074 | 40074 | 40074 | 40074 | 40074 |  |  | 40074 | 40074 | 40074 | 40074 |  | s16 | 1 | 0 | 0 | 0 | R
40075 | BT22 Supply air temp. |  | 40075 | 40075 |  |  | 40075 | 40075 | 40075 | 40075 |  | 40075 | 40075 | 40075 | °C | s16 | 10 | 0 | 0 | 0 | R
40076 | EP30-BT55 Solar Tank Top Temp |  | 40076 | 40076 | [10 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40077 | BT6 external water heater load temp. | Used in DEW, SCA and AHPS Docking accessories |  |  | 40077 | 40077 | [8 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40078 | BT7 external water heater top temp. | Used in DEW, SCA and AHPS Docking accessories |  |  | 40078 | 40078 | [8 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40079 | EB100-BE3 Current |  | 40079 | 40079 | 40079 | 40079 | 40079 | 40079 | 40079 | 40079 |  | 40079 | 40079 | 40079 | A | u32 | 10 | 0 | 0 | 0 | R
40081 | EB100-BE2 Current |  | 40081 | 40081 | 40081 | 40081 | 40081 | 40081 | 40081 | 40081 |  | 40081 | 40081 | 40081 | A | u32 | 10 | 0 | 0 | 0 | R
40083 | EB100-BE1 Current |  | 40083 | 40083 | 40083 | 40083 | 40083 | 40083 | 40083 | 40083 |  | 40083 | 40083 | 40083 | A | u32 | 10 | 0 | 0 | 0 | R
40085 | EB100-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [6 empty] | 40085 | 40085 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40086 | EB100-EP15-BT12 Condensor Out | Condensor out temperature, BT12 | [6 empty] | 40086 | 40086 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40087 | EB100-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [6 empty] | 40087 | 40087 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40088 | EB100-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [6 empty] | 40088 | 40088 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40089 | EB100-EP15-BT17 Suction | Suction temperature, BT17 | [6 empty] | 40089 | 40089 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40100 | EB100-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [6 empty] | 40100 | 40100 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40106 | CL12-BT51 Pool 2 Temp | Pool temperature for Pool 2, BT51 |  |  |  |  | 40106 | 40106 | 40106 | 40106 |  | 40106 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40107 | BT20 Exhaust air temp. 4 | [5 empty] | 40107 | 40107 | 40107 | 40107 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40108 | BT20 Exhaust air temp. 3 | [5 empty] | 40108 | 40108 | 40108 | 40108 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40109 | BT20 Exhaust air temp. 2 | [5 empty] | 40109 | 40109 | 40109 | 40109 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40110 | BT21 Vented air temp. 4 | [5 empty] | 40110 | 40110 | 40110 | 40110 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40111 | BT21 Vented air temp. 3 | [5 empty] | 40111 | 40111 | 40111 | 40111 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40112 | BT21 Vented air temp. 2 | [5 empty] | 40112 | 40112 | 40112 | 40112 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40113 | AZ4-BT26 Temp Collector in FLM 4 | Connected to the FLM module |  |  |  |  | 40113 | 40113 | 40113 | 40113 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40114 | AZ3-BT26 Temp Collector in FLM 3 | Connected to the FLM module |  |  |  |  | 40114 | 40114 | 40114 | 40114 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40115 | AZ2-BT26 Temp Collector in FLM 2 | Connected to the FLM module |  |  |  |  | 40115 | 40115 | 40115 | 40115 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40116 | AZ4-BT27 Temp Collector out FLM 4 | Connected to the FLM module |  |  |  |  | 40116 | 40116 | 40116 | 40116 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40117 | AZ3-BT27 Temp Collector out FLM 3 | Connected to the FLM module |  |  |  |  | 40117 | 40117 | 40117 | 40117 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40118 | AZ2-BT27 Temp Collector out FLM 2 | Connected to the FLM module |  |  |  |  | 40118 | 40118 | 40118 | 40118 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40121 | BT63 Add Supply Temp | [9 empty] | 40121 | 40121 | 40121 | 40121 | ºC | s16 | 10 | 0 | 0 | 0 | R
40122 | BT52 external water heater load temp. | Used in DEH and AHPS Docking accessories | 40122 | 40122 | 40122 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40127 | EP23-BT3 Return temp S4 | Return temperature for system 4 | 40127 | 40127 | 40127 | 40127 | 40127 | 40127 | 40127 | 40127 |  | 40127 | 40127 | 40127 | °C | s16 | 10 | 0 | 0 | 0 | R
40128 | EP22-BT3 Return temp S3 | Return temperature for system 3 | 40128 | 40128 | 40128 | 40128 | 40128 | 40128 | 40128 | 40128 |  | 40128 | 40128 | 40128 | °C | s16 | 10 | 0 | 0 | 0 | R
40129 | EP21-BT3 Return temp S2 | Return temperature for system 2 | 40129 | 40129 | 40129 | 40129 | 40129 | 40129 | 40129 | 40129 |  | 40129 | 40129 | 40129 | °C | s16 | 10 | 0 | 0 | 0 | R
40131 | EB100-EP15-BP8 Pressure Transmitter | Temperature reported by the pressure transmitter | [6 empty] | 40131 | 40131 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40132 | EB100-EP14-BP8 Pressure Transmitter | Temperature reported by the pressure transmitter | [6 empty] | 40132 | 40132 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40141 | AZ2-BT22 Supply air temp. SAM |  |  |  | 40141 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40142 | AZ2-BT23 Outdoor temp. SAM |  |  |  | 40142 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40143 | AZ2-BT68 Flow temp. SAM | Heat medium flow temperature to SAM module |  |  | 40143 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40144 | AZ2-BT69 Return temp. SAM | Heat medium return temperature from SAM module |  |  | 40144 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40145 | EB100-EP15-BT29 Cpr Oil Temp | Compressor oil temperature, BT29 | [6 empty] | 40145 | 40145 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40146 | EB100-EP14-BT29 Cpr Oil Temp | Compressor oil temperature, BT29 |  |  |  |  | 40146 |  | 40146 | 40146 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40147 | BT70 HW Comfort Supply Temp. | Hot water comfort supply temperature, BT70 |  |  |  |  | 40147 | 40147 | 40147 | 40147 |  | 40147 | 40147 |  | °C | s16 | 10 | 0 | 0 | 0 | R
40152 | BT71 Ext. Return Temp | External return temperature, BT71 | [5 empty] | 40152 | 40152 | 40152 | 40152 | 40152 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40154 | EP30-BT51 Solar pool Temp | [12 empty] | 40154 | °C | s16 | 10 | 0 | 0 | 0 | R
40155 | EQ1-BT57 Collector Temp. | External collector temperature, BT57, for ACS |  |  |  |  | 40155 | 40155 |  | 40155 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40156 | EQ1-BT75 Heatdump Temp. | Heating medium dump temperature, BT75, for ACS |  |  |  |  | 40156 | 40156 |  | 40156 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40157 | EP30-BT53 Solar Panel Temp |  |  |  | 40157 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40158 | EP30-BT54 Solar Load Temp |  |  |  | 40158 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40159 | EP47-BT2 Supply temp S8 | Supply temperature for system 8 | 40159 | 40159 | 40159 | 40159 | 40159 | 40159 | 40159 | 40159 |  | 40159 | 40159 | 40159 | °C | s16 | 10 | 0 | 0 | 0 | R
40160 | EP46-BT2 Supply temp S7 | Supply temperature for system 7 | 40160 | 40160 | 40160 | 40160 | 40160 | 40160 | 40160 | 40160 |  | 40160 | 40160 | 40160 | °C | s16 | 10 | 0 | 0 | 0 | R
40161 | EP45-BT2 Supply temp S6 | Supply temperature for system 6 | 40161 | 40161 | 40161 | 40161 | 40161 | 40161 | 40161 | 40161 |  | 40161 | 40161 | 40161 | °C | s16 | 10 | 0 | 0 | 0 | R
40162 | EP44-BT2 Supply temp S5 | Supply temperature for system 5 | 40162 | 40162 | 40162 | 40162 | 40162 | 40162 | 40162 | 40162 |  | 40162 | 40162 | 40162 | °C | s16 | 10 | 0 | 0 | 0 | R
40163 | EP47-BT3 Return temp S8 | Return temperature for system 8 | 40163 | 40163 | 40163 | 40163 | 40163 | 40163 | 40163 | 40163 |  | 40163 | 40163 | 40163 | °C | s16 | 10 | 0 | 0 | 0 | R
40164 | EP46-BT3 Return temp S7 | Return temperature for system 7 | 40164 | 40164 | 40164 | 40164 | 40164 | 40164 | 40164 | 40164 |  | 40164 | 40164 | 40164 | °C | s16 | 10 | 0 | 0 | 0 | R
40165 | EP45-BT3 Return temp S6 | Return temperature for system 6 | 40165 | 40165 | 40165 | 40165 | 40165 | 40165 | 40165 | 40165 |  | 40165 | 40165 | 40165 | °C | s16 | 10 | 0 | 0 | 0 | R
40166 | EP44-BT3 Return temp S5 | Return temperature for system 5 | 40166 | 40166 | 40166 | 40166 | 40166 | 40166 | 40166 | 40166 |  | 40166 | 40166 | 40166 | °C | s16 | 10 | 0 | 0 | 0 | R
40167 | EP47-BT50 Room Temp S8 |  | 40167 | 40167 | 40167 | 40167 | 40167 | 40167 | 40167 | 40167 |  | 40167 | 40167 | 40167 | °C | s16 | 10 | 0 | 0 | 0 | R
40168 | EP46-BT50 Room Temp S7 |  | 40168 | 40168 | 40168 | 40168 | 40168 | 40168 | 40168 | 40168 |  | 40168 | 40168 | 40168 | °C | s16 | 10 | 0 | 0 | 0 | R
40169 | EP45-BT50 Room Temp S6 |  | 40169 | 40169 | 40169 | 40169 | 40169 | 40169 | 40169 | 40169 |  | 40169 | 40169 | 40169 | °C | s16 | 10 | 0 | 0 | 0 | R
40170 | EP44-BT50 Room Temp S5 |  | 40170 | 40170 | 40170 | 40170 | 40170 | 40170 | 40170 | 40170 |  | 40170 | 40170 | 40170 | °C | s16 | 10 | 0 | 0 | 0 | R
40179 | EP10-BT26 Brine in | Brine in temperature in EP10 module | [6 empty] | 40179 | 40179 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
40183 | AZ30-BT23 Outdoor temp. ERS 1 | [5 empty] | 40183 | 40183 | 40183 | 40183 |  | 40183 | 40183 | 40183 | °C | s16 | 10 | 0 | 0 | 0 | R
40185 | BT1 Average, 1h | EB100-BT1 Outdoor temperature average, 1h | 40185 | 40185 | 40185 | 40185 | 40185 | 40185 | 40185 | 40185 | 40185 | 40185 | 40185 | 40185 | °C | s16 | 10 | 0 | 0 | 0 | R
40188 | EP47-BT50 Room Temp S8 Average |  | 40188 | 40188 | 40188 | 40188 | 40188 | 40188 | 40188 | 40188 |  | 40188 | 40188 | 40188 | °C | s16 | 10 | 0 | 0 | 0 | R
40189 | EP46-BT50 Room Temp S7 Average |  | 40189 | 40189 | 40189 | 40189 | 40189 | 40189 | 40189 | 40189 |  | 40189 | 40189 | 40189 | °C | s16 | 10 | 0 | 0 | 0 | R
40190 | EP45-BT50 Room Temp S6 Average |  | 40190 | 40190 | 40190 | 40190 | 40190 | 40190 | 40190 | 40190 |  | 40190 | 40190 | 40190 | °C | s16 | 10 | 0 | 0 | 0 | R
40191 | EP44-BT50 Room Temp S5 Average |  | 40191 | 40191 | 40191 | 40191 | 40191 | 40191 | 40191 | 40191 |  | 40191 | 40191 | 40191 | °C | s16 | 10 | 0 | 0 | 0 | R
40192 | EP23-BT50 Room Temp S4 Average |  | 40192 | 40192 | 40192 | 40192 | 40192 | 40192 | 40192 | 40192 |  | 40192 | 40192 | 40192 | °C | s16 | 10 | 0 | 0 | 0 | R
40193 | EP22-BT50 Room Temp S3 Average |  | 40193 | 40193 | 40193 | 40193 | 40193 | 40193 | 40193 | 40193 |  | 40193 | 40193 | 40193 | °C | s16 | 10 | 0 | 0 | 0 | R
40194 | EP21-BT50 Room Temp S2 Average |  | 40194 | 40194 | 40194 | 40194 | 40194 | 40194 | 40194 | 40194 |  | 40194 | 40194 | 40194 | °C | s16 | 10 | 0 | 0 | 0 | R
40195 | BT50 Room Temp S1 Average |  | 40195 | 40195 | 40195 | 40195 | 40195 | 40195 | 40195 | 40195 | 40195 | 40195 | 40195 | 40195 | °C | s16 | 10 | 0 | 0 | 0 | R
40212 | BT74 Average | BT74 heating cooling sensor average | 40212 | 40212 | 40212 | 40212 | 40212 | 40212 | 40212 | 40212 | 40212 | 40212 | 40212 | 40212 | °C | s16 | 10 | 0 | 0 | 0 | R
40215 | BF1 EP15 Flow | Current flow EP15 | [6 empty] | 40215 | 40215 |  |  |  |  | l/m | s16 | 10 | 0 | 0 | 0 | R
40216 | BT25 Ext. supply temp, cooling | [5 empty] | 40216 | 40216 | 40216 | 40216 | 40216 | 40216 | 40216 |  | °C | s16 | 10 | 0 | 0 | 0 | R
40217 | Calc. Supply S8 | Calculated supply temperature for the climate system | 40217 | 40217 | 40217 | 40217 | 40217 | 40217 | 40217 | 40217 |  | 40217 | 40217 | 40217 | °C | s16 | 10 | 0 | 0 | 0 | R
40218 | Calc. Supply S7 | Calculated supply temperature for the climate system | 40218 | 40218 | 40218 | 40218 | 40218 | 40218 | 40218 | 40218 |  | 40218 | 40218 | 40218 | °C | s16 | 10 | 0 | 0 | 0 | R
40219 | Calc. Supply S6 | Calculated supply temperature for the climate system | 40219 | 40219 | 40219 | 40219 | 40219 | 40219 | 40219 | 40219 |  | 40219 | 40219 | 40219 | °C | s16 | 10 | 0 | 0 | 0 | R
40220 | Calculated Supply S5 | Calculated supply temperature for the climate system | 40220 | 40220 | 40220 | 40220 | 40220 | 40220 | 40220 | 40220 |  | 40220 | 40220 | 40220 | °C | s16 | 10 | 0 | 0 | 0 | R
40221 | Calc. Cooling Supply S8 | Calculated supply temperature in cooling mode for the climate system |  |  |  |  | 40221 | 40221 | 40221 | 40221 | 40221 | 40221 | 40221 | 40221 | °C | s16 | 10 | 0 | 0 | 0 | R
40222 | Calc. Cooling Supply S7 | Calculated supply temperature in cooling mode for the climate system |  |  |  |  | 40222 | 40222 | 40222 | 40222 | 40222 | 40222 | 40222 | 40222 | °C | s16 | 10 | 0 | 0 | 0 | R
40223 | Calc. Cooling Supply S6 | Calculated supply temperature in cooling mode for the climate system |  |  |  |  | 40223 | 40223 | 40223 | 40223 | 40223 | 40223 | 40223 | 40223 | °C | s16 | 10 | 0 | 0 | 0 | R
40224 | Calc. Cooling Supply S5 | Calculated supply temperature in cooling mode for the climate system |  |  |  |  | 40224 | 40224 | 40224 | 40224 | 40224 | 40224 | 40224 | 40224 | °C | s16 | 10 | 0 | 0 | 0 | R
40305 | Mixing Valve State S8 | State of the mixing valve for the climate system | 40305 | 40305 | 40305 | 40305 | 40305 | 40305 | 40305 | 40305 |  | 40305 | 40305 | 40305 |  | u8 | 1 | 0 | 0 | 0 | R
40306 | Mixing Valve State S7 | State of the mixing valve for the climate system | 40306 | 40306 | 40306 | 40306 | 40306 | 40306 | 40306 | 40306 |  | 40306 | 40306 | 40306 |  | u8 | 1 | 0 | 0 | 0 | R
40307 | Mixing Valve State S6 | State of the mixing valve for the climate system | 40307 | 40307 | 40307 | 40307 | 40307 | 40307 | 40307 | 40307 |  | 40307 | 40307 | 40307 |  | u8 | 1 | 0 | 0 | 0 | R
40308 | Mixing Valve State S5 | State of the mixing valve for the climate system | 40308 | 40308 | 40308 | 40308 | 40308 | 40308 | 40308 | 40308 |  | 40308 | 40308 | 40308 |  | u8 | 1 | 0 | 0 | 0 | R
40310 | External ERS 1 accessory relays | Indicates the status of the relays on the ERS accessory. The information is binary encoded. b0: K1, b1: K2, b2: K3, b3: K4 |  |  |  |  | 40310 | 40310 | 40310 | 40310 |  | 40310 | 40310 | 40310 |  | u8 | 1 | 0 | 0 | 0 | R
40311 | External ERS 1 accessory GQ2 speed | Indicates the speed of the GQ2 fan speed on the ERS accessory. |  |  |  |  | 40311 | 40311 | 40311 | 40311 |  | 40311 | 40311 | 40311 | % | u8 | 1 | 0 | 0 | 0 | R
40312 | External ERS 1 accessory GQ3 speed | Indicates the speed of the GQ3 fan speed on the ERS accessory. |  |  |  |  | 40312 | 40312 | 40312 | 40312 |  | 40312 | 40312 | 40312 | % | u8 | 1 | 0 | 0 | 0 | R
40314 | QN10 Need | 0=Heating, 1=Hot water | [6 empty] | 40314 | 40314 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
40316 | Inverter limit status |  |  |  | 40316 |  | 40316 | [8 empty] | u8 | 1 | 0 | 0 | 0 | R
40317 | Inverter drive status |  |  |  | 40317 | 40317 | 40317 |  | 40317 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40321 | Compressor Frequency, Request | The compressor frequency that has been requested by the system |  |  | 40321 | 40321 | 40321 |  | 40321 | [5 empty] | Hz | u16 | 1 | 0 | 0 | 0 | R
40322 | Max Compressor Frequency, Heating | The maximum frequency of the compressor in heating mode |  |  | 40322 | 40322 | 40322 |  | 40322 | [5 empty] | Hz | u16 | 100 | 0 | 0 | 0 | R
40323 | Inverter alarm code |  |  |  | 40323 | 40323 | 40323 |  | 40323 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40324 | Inverter fault code |  |  |  | 40324 | 40324 | 40324 |  | 40324 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40326 | Inverter drive command |  |  |  | 40326 | 40326 | 40326 |  | 40326 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40327 | NIBE Inverter Pic version |  |  |  | 40327 | 40327 | 40327 |  | 40327 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40328 | NIBE Inverter 8051 version |  |  |  | 40328 | 40328 | 40328 |  | 40328 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40329 | NIBE Inverter Def. Wizard |  |  |  | 40329 | 40329 | 40329 |  | 40329 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40330 | NIBE Inverter Mce version |  |  |  | 40330 | 40330 | 40330 |  | 40330 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40331 | NIBE Inverter Hw version |  |  |  | 40331 | 40331 | 40331 |  | 40331 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40332 | NIBE Inverter Hw type |  |  |  | 40332 | 40332 | 40332 |  | 40332 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40339 | External adjustment activated via input S8 |  | 40339 | 40339 | 40339 | 40339 | 40339 | 40339 | 40339 | 40339 |  | 40339 | 40339 | 40339 |  | u8 | 1 | 0 | 0 | 0 | R
40340 | External adjustment activated via input S7 |  | 40340 | 40340 | 40340 | 40340 | 40340 | 40340 | 40340 | 40340 |  | 40340 | 40340 | 40340 |  | u8 | 1 | 0 | 0 | 0 | R
40341 | External adjustment activated via input S6 |  | 40341 | 40341 | 40341 | 40341 | 40341 | 40341 | 40341 | 40341 |  | 40341 | 40341 | 40341 |  | u8 | 1 | 0 | 0 | 0 | R
40342 | External adjustment activated via input S5 |  | 40342 | 40342 | 40342 | 40342 | 40342 | 40342 | 40342 | 40342 |  | 40342 | 40342 | 40342 |  | u8 | 1 | 0 | 0 | 0 | R
40364 | AHPS Docking blocked | 0 = unblocked, 1 = blocked |  |  | 40364 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
40365 | Extra heating system pump S8 |  | 40365 | 40365 | 40365 | 40365 | 40365 | 40365 | 40365 | 40365 |  | 40365 | 40365 | 40365 |  | u8 | 1 | 0 | 0 | 0 | R
40366 | Extra heating system pump S7 |  | 40366 | 40366 | 40366 | 40366 | 40366 | 40366 | 40366 | 40366 |  | 40366 | 40366 | 40366 |  | u8 | 1 | 0 | 0 | 0 | R
40367 | Extra heating system pump S6 |  | 40367 | 40367 | 40367 | 40367 | 40367 | 40367 | 40367 | 40367 |  | 40367 | 40367 | 40367 |  | u8 | 1 | 0 | 0 | 0 | R
40368 | Extra heating system pump S5 |  | 40368 | 40368 | 40368 | 40368 | 40368 | 40368 | 40368 | 40368 |  | 40368 | 40368 | 40368 |  | u8 | 1 | 0 | 0 | 0 | R
40369 | Extra cooling HPAC, ACS | [5 empty] | 40369 | 40369 | 40369 | 40369 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
40370 | AHPS Docking accessory relays | 0=Off, 1=On. b0:EM1-GP4, b1:Cool need, b2:QN32, b3:QN11 close, b4:EP30-GP4, b5:QN11 open ,b6:Ext add |  |  | 40370 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
40607 | Heat Meter - HW Cpr and Add EP15 | Accumulated energy production as calculated by the heat meter | [6 empty] | 40607 | 40607 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
40609 | Heat Meter - Heat Cpr and Add EP15 | Accumulated energy production as calculated by the heat meter | [6 empty] | 40609 | 40609 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
40611 | Heat Meter - Cooling Cpr EP15 | Accumulated energy production as calculated by the heat meter | [6 empty] | 40611 | 40611 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
40613 | Heat Meter - Pool Cpr EP15 | Accumulated energy production as calculated by the heat meter | [6 empty] | 40613 | 40613 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
40615 | Heat Meter - HW Cpr EP15 | Accumulated energy production as calculated by the heat meter | [6 empty] | 40615 | 40615 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
40617 | Heat Meter - Heat Cpr EP15 | Accumulated energy production as calculated by the heat meter | [6 empty] | 40617 | 40617 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
40625 | BT82 HW Comfort Return Temp | [5 empty] | 40625 | 40625 | 40625 | 40625 |  | 40625 | 40625 |  | °C | s16 | 10 | 0 | 0 | 0 | R
40626 | BT83 HW Comfort Cylinder Temp | [5 empty] | 40626 | 40626 | 40626 | 40626 |  | 40626 | 40626 |  | °C | s16 | 10 | 0 | 0 | 0 | R
40627 | MP brine pump. | Motor protection brine pump | [7 empty] | 40627 | [5 empty] | s16 | 1 | 0 | 0 | 0 | R
40647 | EB108-EP15 Tot. Cooling op.time compr | [6 empty] | 40647 | 40647 | 40647 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40649 | EB108-EP15 Tot. Pool1 op.time compr | [6 empty] | 40649 | 40649 | 40649 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40651 | EB108-EP15 Tot. Pool2 op.time compr | [6 empty] | 40651 | 40651 | 40651 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40653 | EB108-EP14 Tot. Cooling op.time compr | [6 empty] | 40653 | 40653 | 40653 |  | 40653 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40655 | EB108-EP14 Tot. Pool1 op.time compr | [6 empty] | 40655 | 40655 | 40655 |  | 40655 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40657 | EB108-EP14 Tot. Pool2 op.time compr | [6 empty] | 40657 | 40657 | 40657 |  | 40657 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40659 | EB107-EP15 Tot. Cooling op.time compr | [6 empty] | 40659 | 40659 | 40659 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40661 | EB107-EP15 Tot. Pool1 op.time compr | [6 empty] | 40661 | 40661 | 40661 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40663 | EB107-EP15 Tot. Pool2 op.time compr | [6 empty] | 40663 | 40663 | 40663 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40665 | EB107-EP14 Tot. Cooling op.time compr | [6 empty] | 40665 | 40665 | 40665 |  | 40665 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40667 | EB107-EP14 Tot. Pool1 op.time compr | [6 empty] | 40667 | 40667 | 40667 |  | 40667 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40669 | EB107-EP14 Tot. Pool2 op.time compr | [6 empty] | 40669 | 40669 | 40669 |  | 40669 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40671 | EB106-EP15 Tot. Cooling op.time compr | [6 empty] | 40671 | 40671 | 40671 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40673 | EB106-EP15 Tot. Pool1 op.time compr | [6 empty] | 40673 | 40673 | 40673 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40675 | EB106-EP15 Tot. Pool2 op.time compr | [6 empty] | 40675 | 40675 | 40675 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40677 | EB106-EP14 Tot. Cooling op.time compr | [6 empty] | 40677 | 40677 | 40677 |  | 40677 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40679 | EB106-EP14 Tot. Pool1 op.time compr | [6 empty] | 40679 | 40679 | 40679 |  | 40679 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40681 | EB106-EP14 Tot. Pool2 op.time compr | [6 empty] | 40681 | 40681 | 40681 |  | 40681 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40683 | EB105-EP15 Tot. Cooling op.time compr | [6 empty] | 40683 | 40683 | 40683 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40685 | EB105-EP15 Tot. Pool1 op.time compr | [6 empty] | 40685 | 40685 | 40685 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40687 | EB105-EP15 Tot. Pool2 op.time compr | [6 empty] | 40687 | 40687 | 40687 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40689 | EB105-EP14 Tot. Cooling op.time compr | [6 empty] | 40689 | 40689 | 40689 |  | 40689 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40691 | EB105-EP14 Tot. Pool1 op.time compr | [6 empty] | 40691 | 40691 | 40691 |  | 40691 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40693 | EB105-EP14 Tot. Pool2 op.time compr | [6 empty] | 40693 | 40693 | 40693 |  | 40693 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40695 | EB104-EP15 Tot. Cooling op.time compr | [6 empty] | 40695 | 40695 | 40695 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40697 | EB104-EP15 Tot. Pool1 op.time compr | [6 empty] | 40697 | 40697 | 40697 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40699 | EB104-EP15 Tot. Pool2 op.time compr | [6 empty] | 40699 | 40699 | 40699 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40701 | EB104-EP14 Tot. Cooling op.time compr | [6 empty] | 40701 | 40701 | 40701 |  | 40701 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40703 | EB104-EP14 Tot. Pool1 op.time compr | [6 empty] | 40703 | 40703 | 40703 |  | 40703 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40705 | EB104-EP14 Tot. Pool2 op.time compr | [6 empty] | 40705 | 40705 | 40705 |  | 40705 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40707 | EB103-EP15 Tot. Cooling op.time compr | [6 empty] | 40707 | 40707 | 40707 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40709 | EB103-EP15 Tot. Pool1 op.time compr | [6 empty] | 40709 | 40709 | 40709 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40711 | EB103-EP15 Tot. Pool2 op.time compr | [6 empty] | 40711 | 40711 | 40711 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40713 | EB103-EP14 Tot. Cooling op.time compr | [6 empty] | 40713 | 40713 | 40713 |  | 40713 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40715 | EB103-EP14 Tot. Pool1 op.time compr | [6 empty] | 40715 | 40715 | 40715 |  | 40715 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40717 | EB103-EP14 Tot. Pool2 op.time compr | [6 empty] | 40717 | 40717 | 40717 |  | 40717 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40719 | EB102-EP15 Tot. Cooling op.time compr | [6 empty] | 40719 | 40719 | 40719 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40721 | EB102-EP15 Tot. Pool1 op.time compr | [6 empty] | 40721 | 40721 | 40721 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40723 | EB102-EP15 Tot. Pool2 op.time compr | [6 empty] | 40723 | 40723 | 40723 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40725 | EB102-EP14 Tot. Cooling op.time compr | [6 empty] | 40725 | 40725 | 40725 |  | 40725 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40727 | EB102-EP14 Tot. Pool1 op.time compr | [6 empty] | 40727 | 40727 | 40727 |  | 40727 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40729 | EB102-EP14 Tot. Pool2 op.time compr | [6 empty] | 40729 | 40729 | 40729 |  | 40729 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
40731 | EB101-EP15 Tot. Cooling op.time compr | [6 empty] | 40731 | 40731 | 40731 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40733 | EB101-EP15 Tot. Pool1 op.time compr | [6 empty] | 40733 | 40733 | 40733 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40735 | EB101-EP15 Tot. Pool2 op.time compr | [6 empty] | 40735 | 40735 | 40735 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
40737 | EB101-EP14 Tot. Cooling op.time compr | [6 empty] | 40737 | 40737 | 40737 | 40737 | 40737 | 40737 | 40737 | h | u32 | 1 | 0 | 9999999 | 0 | R
40739 | EB101-EP14 Tot. Pool1 op.time compr | [6 empty] | 40739 | 40739 | 40739 | 40739 | 40739 | 40739 | 40739 | h | u32 | 1 | 0 | 9999999 | 0 | R
40741 | EB101-EP14 Tot. Pool2 op.time compr | [6 empty] | 40741 | 40741 | 40741 | 40741 | 40741 | 40741 | 40741 | h | u32 | 1 | 0 | 9999999 | 0 | R
40755 | Tot. ext. HW add op.time | Total external hw-electric additive operation time | 40755 | 40755 | 40755 | 40755 | 40755 | 40755 | 40755 | 40755 | 40755 | 40755 | 40755 | 40755 | h | s32 | 10 | 0 | 9999999 | 0 | R
40760 | Hz unlimited |  |  |  | 40760 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
40762 | Reg. state AHPS Docking shunt | 10 = Off, 20 = Running |  |  | 40762 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
40763 | AHPS Docking calc. supply temp. |  |  |  | 40763 | [10 empty] | s16 | 10 | 0 | 0 | 0 | R
40769 | Heat Meter - Pool2 Cpr EP15 | Accumulated energy production as calculated by the heat meter | [6 empty] | 40769 | 40769 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
40771 | Heat Meter - Pool2 Cpr EP14 | Accumulated energy production as calculated by the heat meter |  |  | 40771 | 40771 | 40771 | 40771 | 40771 | 40771 |  |  | 40771 | 40771 | kWh | u32 | 10 | 0 | 0 | 0 | R
40775 | EB108 Cpr Frequency Desired F2040 | The desired frequency as shown in service info | [8 empty] | 40775 | 40775 | 40775 | 40775 | Hz | u8 | 1 | 0 | 0 | 0 | R
40776 | EB107 Cpr Frequency Desired F2040 | The desired frequency as shown in service info | [8 empty] | 40776 | 40776 | 40776 | 40776 | Hz | u8 | 1 | 0 | 0 | 0 | R
40777 | EB106 Cpr Frequency Desired F2040 | The desired frequency as shown in service info | [8 empty] | 40777 | 40777 | 40777 | 40777 | Hz | u8 | 1 | 0 | 0 | 0 | R
40778 | EB105 Cpr Frequency Desired F2040 | The desired frequency as shown in service info | [8 empty] | 40778 | 40778 | 40778 | 40778 | Hz | u8 | 1 | 0 | 0 | 0 | R
40779 | EB104 Cpr Frequency Desired F2040 | The desired frequency as shown in service info | [8 empty] | 40779 | 40779 | 40779 | 40779 | Hz | u8 | 1 | 0 | 0 | 0 | R
40780 | EB103 Cpr Frequency Desired F2040 | The desired frequency as shown in service info | [8 empty] | 40780 | 40780 | 40780 | 40780 | Hz | u8 | 1 | 0 | 0 | 0 | R
40781 | EB102 Cpr Frequency Desired F2040 | The desired frequency as shown in service info | [8 empty] | 40781 | 40781 | 40781 | 40781 | Hz | u8 | 1 | 0 | 0 | 0 | R
40782 | EB101 Cpr Frequency Desired F2040 | The desired frequency as shown in service info | [8 empty] | 40782 | 40782 | 40782 | 40782 | Hz | u8 | 1 | 0 | 0 | 0 | R
40792 | OPT state | Indicates the state of the boiler connected through the OPT accessory. |  |  |  |  | 40792 | 40792 | 40792 | 40792 |  | 40792 | 40792 | 40792 |  | u8 | 1 | 0 | 0 | 0 | R
40793 | OPT version | Version of the OPT PCBA software |  |  |  |  | 40793 | 40793 | 40793 | 40793 |  | 40793 | 40793 | 40793 |  | u16 | 1 | 0 | 0 | 0 | R
40801 | OPT rel. modulation level | OPT relative modulation level |  |  |  |  | 40801 | 40801 | 40801 | 40801 |  | 40801 | 40801 | 40801 | % | s16 | 10 | 0 | 0 | 0 | R
40802 | OPT boiler temperature | OPT boiler temperature |  |  |  |  | 40802 | 40802 | 40802 | 40802 |  | 40802 | 40802 | 40802 | °C | s16 | 10 | 0 | 0 | 0 | R
40806 | OPT boiler op. time | OPT boiler operation time |  |  |  |  | 40806 | 40806 | 40806 | 40806 |  | 40806 | 40806 | 40806 | h | u16 | 1 | 0 | 0 | 0 | R
40813 | Compressor slow down reason | Bitmap telling the reason to why the compressor slows down. b0:inverter b1:brine b2:current b3:high cond b4:hot gas b5:evaporator |  |  |  | 40813 | 40813 | [8 empty] | u8 | 1 | 0 | 0 | 0 | R
40818 | Available Heat Compressors | Number of compressors available for heating |  |  |  | 40818 |  | 40818 | 40818 | 40818 |  | 40818 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
40819 | Available Hot Water Compressors | Number of compressors available for to hot water |  |  |  | 40819 |  | 40819 | 40819 | 40819 |  | 40819 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
40820 | Available Pool 1 Compressors | Number of compressors available for pool 1 | [5 empty] | 40820 | 40820 | 40820 |  | 40820 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
40821 | Available Pool 2 Compressors | Number of compressors available for pool 2 | [5 empty] | 40821 | 40821 | 40821 |  | 40821 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
40822 | Available Cool Compressors | Number of compressors available for cooling | [5 empty] | 40822 | 40822 | 40822 |  | 40822 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
40823 | Available External Compressors | Number of compressors available for external control | [5 empty] | 40823 | 40823 | 40823 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
40834 | BM1 Humidity | [5 empty] | 40834 | 40834 | 40834 | 40834 |  | 40834 | 40834 | 40834 | % | s16 | 10 | 0 | 0 | 0 | R
40856 | BM1 BT50 Room temp. | [5 empty] | 40856 | 40856 | 40856 | 40856 |  | 40856 | 40856 | 40856 | °C | s16 | 10 | 0 | 0 | 0 | R
40857 | BM1 Pressure | [5 empty] | 40857 | 40857 | 40857 | 40857 |  | 40857 | 40857 | 40857 | kPa | s16 | 10 | 0 | 0 | 0 | R
40858 | BM1 Dewpoint | [5 empty] | 40858 | 40858 | 40858 | 40858 |  | 40858 | 40858 | 40858 | °C | s16 | 10 | 0 | 0 | 0 | R
40868 | +Adjust AUX Port |  | 40868 | 40868 | 40868 | [9 empty] | 1 | u8 | 1 | 0 | 0 | 0 | R
40870 | +Adjust OP mode | Tells if plusadjust system calls for heat or cool | 40870 | 40870 | 40870 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
40871 | +Adjust Comfort mode | Which comfort mode | 40871 | 40871 | 40871 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
40872 | +Adjust Parallell adjustment | requested adjustment | 40872 | 40872 | 40872 | [10 empty] | s8 | 1 | 0 | 0 | 0 | R
40873 | +Adjust Humidity | Humidity | 40873 | 40873 | 40873 | [9 empty] | %RH | s16 | 10 | 0 | 0 | 0 | R
40874 | +Adjust Temp indoor | Average of all room sensors | 40874 | 40874 | 40874 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40875 | +Adjust Temp outdoor | Outdoor temp | 40875 | 40875 | 40875 | [9 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
40876 | +Adjust Version | PCA input version | 40876 | 40876 | 40876 | [10 empty] | u16 | 1 | 0 | 0 | 0 | R
40877 | +Adjust Activated | If plusadjust accessory is activated | 40877 | 40877 | 40877 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
40878 | +Adjust Need | If plusadjust system calls for heat | 40878 | 40878 | 40878 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
40879 | +Adjust Parallell factor |  | 40879 | 40879 | [10 empty] | 1 | s8 | 1 | 1 | 10 | 5 | R/W
40880 | +Adjust Max change | Largest allowed change | 40880 | 40880 | [11 empty] | s8 | 1 | 0 | 0 | 0 | R/W
40881 | +Adjust Affect system8 | System affected by paralell change | 40881 | 40881 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
40882 | +Adjust Affect system7 | System affected by paralell change | 40882 | 40882 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
40883 | +Adjust Affect system6 | System affected by paralell change | 40883 | 40883 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
40884 | +Adjust Affect system5 | System affected by paralell change | 40884 | 40884 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
40885 | +Adjust Affect system4 | System affected by paralell change | 40885 | 40885 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
40886 | +Adjust Affect system3 | System affected by paralell change | 40886 | 40886 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
40887 | +Adjust Affect system2 | System affected by paralell change | 40887 | 40887 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
40888 | +Adjust Affect system1 | System affected by paralell change | 40888 | 40888 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
40889 | BT64 Average | BT64 Cooling supply average | 40889 | 40889 | 40889 | 40889 | 40889 | 40889 | 40889 | 40889 | 40889 | 40889 | 40889 | 40889 | °C | s16 | 10 | 0 | 0 | 0 | R
40912 | EQ1 State ACS Thermostat | 10=off,40=active wait,50=active |  |  |  |  | 40912 | 40912 | 40912 | 40912 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
40913 | EQ1 State ACS Thermostat Heat Dump | 10=shunt off,20=shunt open,30=shunt closed |  |  |  |  | 40913 | 40913 | 40913 | 40913 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
40918 | EB100-FD3 Temperature limiter |  |  |  | 40918 | 40918 | [9 empty] | s16 | 1 | 0 | 0 | 0 | R
40919 | State Outdoor Air Mixing | The state of the Outdoor Air Mixing function |  |  |  | 40919 | [9 empty] | u8 | 1 | 0 | 0 | 0 | R
40928 | AZ10 Number of Starts | [10 empty] | 40928 | 40928 | 40928 |  | u32 | 1 | 0 | 9999999 | 0 | R
40930 | AZ10 Total Operating Time | [10 empty] | 40930 | 40930 | 40930 | h | u32 | 1 | 0 | 9999999 | 0 | R
40932 | Kind of defrost | Kind of defrost: 0 = No defrost, 1 = Passive defrost, 2 = Active defrost |  |  | 40932 | 40932 | [9 empty] | u8 | 1 | 0 | 0 | 0 | R
40934 | Active defrosting time | Calculated time for active defrosting of the compressor. |  |  | 40934 | 40934 | [8 empty] | s | s16 | 1 | 0 | 0 | 0 | R
40935 | Passive defrosting time | Calculated time for passive defrosting of the compressor. |  |  | 40935 | 40935 | [8 empty] | s | s16 | 1 | 0 | 0 | 0 | R
40940 | Degree Minutes (32 bit) | Degree minutes, 32bit value. Full resolution. |  |  | 40940 | 40940 | 40940 | 40940 | 40940 | 40940 | 40940 | 40940 | 40940 | 40940 |  | s32 | 10 | -30000 | 30000 | 0 | R/W
40942 | External ERS 1 accessory block status | Indicates if the ERS accessory is externaly blocked. |  |  |  |  | 40942 | 40942 | 40942 | 40942 |  | 40942 | 40942 | 40942 |  | u8 | 1 | 0 | 0 | 0 | R
40943 | External ERS 1 accessory EB17 | Indicates if the status of ERS accessory EB17. I = closed, 0 = open. |  |  |  |  | 40943 | 40943 | 40943 | 40943 |  | 40943 | 40943 | 40943 |  | u8 | 1 | 0 | 0 | 0 | R
40947 | F135 AZ10-BT12 Cond. out | [10 empty] | 40947 | 40947 | 40947 | °C | s16 | 10 | 0 | 0 | 0 | R
40948 | F135 AZ10-BT13 Cond. in | [10 empty] | 40948 | 40948 | 40948 | °C | s16 | 10 | 0 | 0 | 0 | R
40949 | F135 AZ10-BT16 Evaporator temp | [10 empty] | 40949 | 40949 | 40949 | °C | s16 | 10 | 0 | 0 | 0 | R
40950 | F135 AZ10-BT76 Defrosting temp | [10 empty] | 40950 | 40950 | 40950 | °C | s16 | 10 | 0 | 0 | 0 | R
40951 | F135 AZ10-BT77 Air in temp | [10 empty] | 40951 | 40951 | 40951 | °C | s16 | 10 | 0 | 0 | 0 | R
40952 | F135 AZ10 Active Alarm Number | [10 empty] | 40952 | 40952 | 40952 |  | u16 | 1 | 0 | 0 | 0 | R
40954 | F135 AZ10 Defrosting | 1 = Yes, 0 = No | [9 empty] | 40954 | 40954 | 40954 |  | u8 | 1 | 0 | 0 | 0 | R
40955 | F135 AZ10 Relay Status | [10 empty] | 40955 | 40955 | 40955 |  | u8 | 1 | 0 | 0 | 0 | R
40961 | F135 AZ10 Pump Speed | [10 empty] | 40961 | 40961 | 40961 | % | u8 | 1 | 0 | 0 | 0 | R
40962 | F135 AZ10 Fan Speed | [10 empty] | 40962 | 40962 | 40962 | % | u8 | 1 | 0 | 0 | 0 | R
40964 | F135 AZ10 Version | [10 empty] | 40964 | 40964 | 40964 |  | u16 | 1 | 0 | 0 | 0 | R
40993 | Inverter min speed |  |  |  | 40993 | 40993 | 40993 |  | 40993 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40994 | Inverter max speed |  |  |  | 40994 | 40994 | 40994 |  | 40994 | [6 empty] | u16 | 1 | 0 | 0 | 0 | R
40995 | External Energy Meter 2 Accumulated Energy |  |  |  | 40995 | 40995 | 40995 | 40995 | 40995 | 40995 |  | 40995 | 40995 | 40995 | kWh | u32 | 100 | 0 | 2147483647 | 0 | R
40997 | External Energy Meter 1 Accumulated Energy |  |  |  | 40997 | 40997 | 40997 | 40997 | 40997 | 40997 |  | 40997 | 40997 | 40997 | kWh | u32 | 100 | 0 | 2147483647 | 0 | R
41000 | EB101 F2120 Alarm Number | [9 empty] | 41000 | 41000 | 41000 | 41000 |  | u8 | 1 | 0 | 0 | 0 | R
41002 | EB101 F2120 Fan Speed | F2120 Current Fan Speed | [8 empty] | 41002 | 41002 | 41002 | 41002 | rpm | u16 | 1 | 0 | 0 | 0 | R
41003 | EB101 F2120 Max Fan Speed | F2120 Current Max Fan Speed | [8 empty] | 41003 | 41003 | 41003 | 41003 | rpm | u16 | 1 | 0 | 0 | 0 | R
41004 | EB101 F2120 Min Fan Speed | F2120 Current Min Fan Speed | [8 empty] | 41004 | 41004 | 41004 | 41004 | rpm | u16 | 1 | 0 | 0 | 0 | R
41005 | EB101 F2120 Max Compressor Speed | F2120 Current Max Compressor Speed | [8 empty] | 41005 | 41005 | 41005 | 41005 | Hz | u16 | 10 | 0 | 0 | 0 | R
41006 | EB101 F2120 Min Compressor Speed | F2120 Current Min Compressor Speed | [8 empty] | 41006 | 41006 | 41006 | 41006 | Hz | u16 | 10 | 0 | 0 | 0 | R
41007 | EB101 F2120 Calculated Power | F2120 Current Calculated Power | [8 empty] | 41007 | 41007 | 41007 | 41007 | kW | u16 | 10 | 0 | 0 | 0 | R
41008 | EB101 F2120 Time To Defrost | [9 empty] | 41008 | 41008 | 41008 | 41008 | min | u16 | 1 | 0 | 0 | 0 | R
41026 | EB100-Adjusted BS1 Air flow |  |  |  | 41026 | 41026 | [9 empty] | s16 | 10 | 0 | 0 | 0 | R
41027 | Humidity average | Humidity average | 41027 | 41027 | 41027 | 41027 | 41027 | 41027 | 41027 | 41027 | 41027 | 41027 | 41027 | 41027 | % | s16 | 10 | 0 | 0 | 0 | R
41050 | EB108-EP14-BP8 LP Dew Pressure Sensor | [10 empty] | 41050 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41051 | EB108-EP14-BP9 HP Dew Pressure Sensor | [10 empty] | 41051 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41052 | EB108-EP14-BT81 Evi Temp | [10 empty] | 41052 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41053 | EB108-EP14-BP11 Evi Pressure | [10 empty] | 41053 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
41054 | EB108-EP14-BP11 Evi Dew Pressure | [10 empty] | 41054 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41055 | EB108-EP14-BT84 Evaptor temp | [10 empty] | 41055 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41056 | EB108-EP14 Fan Status | [10 empty] | 41056 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41057 | EB108-EP14 Fan Set | [10 empty] | 41057 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41066 | EB107-EP14-BP8 LP Dew Pressure Sensor | [10 empty] | 41066 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41067 | EB107-EP14-BP9 HP Dew Pressure Sensor | [10 empty] | 41067 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41068 | EB107-EP14-BT81 Evi Temp | [10 empty] | 41068 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41069 | EB107-EP14-BP11 Evi Pressure | [10 empty] | 41069 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
41070 | EB107-EP14-BP11 Evi Dew Pressure | [10 empty] | 41070 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41071 | EB107-EP14-BT84 Evaptor temp | [10 empty] | 41071 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41072 | EB107-EP14 Fan Status | [10 empty] | 41072 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41073 | EB107-EP14 Fan Set | [10 empty] | 41073 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41082 | EB106-EP14-BP8 LP Dew Pressure Sensor | [10 empty] | 41082 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41083 | EB106-EP14-BP9 HP Dew Pressure Sensor | [10 empty] | 41083 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41084 | EB106-EP14-BT81 Evi Temp | [10 empty] | 41084 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41085 | EB106-EP14-BP11 Evi Pressure | [10 empty] | 41085 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
41086 | EB106-EP14-BP11 Evi Dew Pressure | [10 empty] | 41086 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41087 | EB106-EP14-BT84 Evaptor temp | [10 empty] | 41087 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41088 | EB106-EP14 Fan Status | [10 empty] | 41088 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41089 | EB106-EP14 Fan Set | [10 empty] | 41089 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41098 | EB105-EP14-BP8 LP Dew Pressure Sensor | [10 empty] | 41098 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41099 | EB105-EP14-BP9 HP Dew Pressure Sensor | [10 empty] | 41099 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41100 | EB105-EP14-BT81 Evi Temp | [10 empty] | 41100 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41101 | EB105-EP14-BP11 Evi Pressure | [10 empty] | 41101 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
41102 | EB105-EP14-BP11 Evi Dew Pressure | [10 empty] | 41102 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41103 | EB105-EP14-BT84 Evaptor temp | [10 empty] | 41103 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41104 | EB105-EP14 Fan Status | [10 empty] | 41104 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41105 | EB105-EP14 Fan Set | [10 empty] | 41105 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41114 | EB104-EP14-BP8 LP Dew Pressure Sensor | [10 empty] | 41114 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41115 | EB104-EP14-BP9 HP Dew Pressure Sensor | [10 empty] | 41115 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41116 | EB104-EP14-BT81 Evi Temp | [10 empty] | 41116 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41117 | EB104-EP14-BP11 Evi Pressure | [10 empty] | 41117 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
41118 | EB104-EP14-BP11 Evi Dew Pressure | [10 empty] | 41118 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41119 | EB104-EP14-BT84 Evaptor temp | [10 empty] | 41119 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41120 | EB104-EP14 Fan Status | [10 empty] | 41120 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41121 | EB104-EP14 Fan Set | [10 empty] | 41121 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41130 | EB103-EP14-BP8 LP Dew Pressure Sensor | [10 empty] | 41130 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41131 | EB103-EP14-BP9 HP Dew Pressure Sensor | [10 empty] | 41131 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41132 | EB103-EP14-BT81 Evi Temp | [10 empty] | 41132 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41133 | EB103-EP14-BP11 Evi Pressure | [10 empty] | 41133 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
41134 | EB103-EP14-BP11 Evi Dew Pressure | [10 empty] | 41134 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41135 | EB103-EP14-BT84 Evaptor temp | [10 empty] | 41135 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41136 | EB103-EP14 Fan Status | [10 empty] | 41136 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41137 | EB103-EP14 Fan Set | [10 empty] | 41137 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41146 | EB102-EP14-BP8 LP Dew Pressure Sensor | [10 empty] | 41146 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41147 | EB102-EP14-BP9 HP Dew Pressure Sensor | [10 empty] | 41147 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41148 | EB102-EP14-BT81 Evi Temp | [10 empty] | 41148 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41149 | EB102-EP14-BP11 Evi Pressure | [10 empty] | 41149 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
41150 | EB102-EP14-BP11 Evi Dew Pressure | [10 empty] | 41150 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41151 | EB102-EP14-BT84 Evaptor temp | [10 empty] | 41151 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41152 | EB102-EP14 Fan Status | [10 empty] | 41152 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41153 | EB102-EP14 Fan Set | [10 empty] | 41153 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41162 | EB101-EP14-BP8 LP Dew Pressure Sensor | [9 empty] | 41162 | 41162 | 41162 | 41162 | °C | s16 | 10 | 0 | 0 | 0 | R
41163 | EB101-EP14-BP9 HP Dew Pressure Sensor | [9 empty] | 41163 | 41163 | 41163 | 41163 | °C | s16 | 10 | 0 | 0 | 0 | R
41164 | EB101-EP14-BT81 Evi Temp | [9 empty] | 41164 | 41164 | 41164 | 41164 | °C | s16 | 10 | 0 | 0 | 0 | R
41165 | EB101-EP14-BP11 Evi Pressure | [9 empty] | 41165 | 41165 | 41165 | 41165 | bar | s16 | 10 | 0 | 0 | 0 | R
41166 | EB101-EP14-BP11 Evi Dew Pressure | [9 empty] | 41166 | 41166 | 41166 | 41166 | °C | s16 | 10 | 0 | 0 | 0 | R
41167 | EB101-EP14-BT84 Evaptor temp | [9 empty] | 41167 | 41167 | 41167 | 41167 | °C | s16 | 10 | 0 | 0 | 0 | R
41168 | EB101-EP14 Fan Status | [9 empty] | 41168 | 41168 | 41168 | 41168 |  | u8 | 1 | 0 | 0 | 0 | R
41169 | EB101-EP14 Fan Set | [9 empty] | 41169 | 41169 | 41169 | 41169 | rpm | u16 | 1 | 0 | 0 | 0 | R
41186 | Set point OPT boiler | Set point OPT boiler |  |  |  |  | 41186 | 41186 | 41186 | 41186 |  | 41186 | 41186 | 41186 | °C | s16 | 10 | 0 | 0 | 0 | R
41187 | AZ10 High Condenser Out Alarm | [10 empty] | 41187 | 41187 | 41187 |  | u8 | 1 | 0 | 0 | 0 | R
41188 | AZ10 High Condenser In Alarm | [10 empty] | 41188 | 41188 | 41188 |  | u8 | 1 | 0 | 0 | 0 | R
41189 | AA20-BE5 EME10 Current |  | 41189 | 41189 | 41189 | 41189 | 41189 | 41189 | [6 empty] | A | s16 | 10 | 0 | 0 | 0 | R
41190 | AA20-BE5 EME10 Average Current |  | 41190 | 41190 | 41190 | 41190 | 41190 | 41190 | [6 empty] | A | s16 | 10 | 0 | 0 | 0 | R
41191 | PV Panel State |  | 41191 | 41191 | 41191 | 41191 | 41191 | 41191 | 41191 | 41191 | 41191 | 41191 | 41191 | 41191 |  | u8 | 1 | 0 | 0 | 0 | R
41210 | AZ4-BT50 Room temp | AZ4-BT50 Room temp |  |  |  |  | 41210 | 41210 | 41210 | 41210 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41211 | AZ3-BT50 Room temp | AZ3-BT50 Room temp |  |  |  |  | 41211 | 41211 | 41211 | 41211 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41212 | AZ2-BT50 Room temp | AZ2-BT50 Room temp |  |  |  |  | 41212 | 41212 | 41212 | 41212 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41213 | AZ1-BT50 Room temp | AZ1-BT50 Room temp |  |  |  |  | 41213 | 41213 | 41213 | 41213 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41214 | OEK accessory block status | Indicates if the OEK accessory is externally blocked. |  |  | 41214 | 41214 | [9 empty] | u8 | 1 | 0 | 0 | 0 | R
41215 | OEK state | Indicates the internal state of the OEK accessory. Inactive states: 10, 40:. Active states: 20, 30, 50, 60, 70. |  |  |  | 41215 | [9 empty] | u8 | 1 | 0 | 0 | 0 | R
41216 | OEK accessory relays | b0:QN38 outdoor air damper, b1-b7: 0 (not used) |  |  |  | 41216 | [9 empty] | u8 | 1 | 0 | 0 | 0 | R
41256 | Fan speed current | The current fan speed after scheduling and blocks are considered | 41256 | 41256 | 41256 | 41256 | 41256 | 41256 | 41256 | 41256 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
41257 | Fan speed current | The current fan speed after scheduling and blocks are considered | 41257 | 41257 | 41257 | 41257 | 41257 | 41257 | 41257 | 41257 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
41258 | Fan speed current | The current fan speed after scheduling and blocks are considered | 41258 | 41258 | 41258 | 41258 | 41258 | 41258 | 41258 | 41258 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
41265 | Smart Home Mode | Current smart home mode, 0=Default,1=Away from home,2=Vacation | 41265 | 41265 | 41265 | 41265 | 41265 | 41265 | 41265 | 41265 | 41265 | 41265 | 41265 | 41265 |  | u8 | 1 | 0 | 0 | 0 | R
41266 | Offset to smart home system | Offset to smart home system | 41266 | 41266 | 41266 | 41266 | 41266 | 41266 | 41266 | 41266 | 41266 | 41266 | 41266 | 41266 | °C | s8 | 10 | 0 | 0 | 0 | R
41267 | Smart Home ctrl syst 8 | Smart Home is controlling the system | 41267 | 41267 | 41267 | 41267 | 41267 | 41267 | 41267 | 41267 | 41267 | 41267 | 41267 | 41267 |  | u8 | 1 | 0 | 0 | 0 | R
41268 | Smart Home ctrl syst 7 | Smart Home is controlling the system | 41268 | 41268 | 41268 | 41268 | 41268 | 41268 | 41268 | 41268 | 41268 | 41268 | 41268 | 41268 |  | u8 | 1 | 0 | 0 | 0 | R
41269 | Smart Home ctrl syst 6 | Smart Home is controlling the system | 41269 | 41269 | 41269 | 41269 | 41269 | 41269 | 41269 | 41269 | 41269 | 41269 | 41269 | 41269 |  | u8 | 1 | 0 | 0 | 0 | R
41270 | Smart Home ctrl syst 5 | Smart Home is controlling the system | 41270 | 41270 | 41270 | 41270 | 41270 | 41270 | 41270 | 41270 | 41270 | 41270 | 41270 | 41270 |  | u8 | 1 | 0 | 0 | 0 | R
41271 | Smart Home ctrl syst 4 | Smart Home is controlling the system | 41271 | 41271 | 41271 | 41271 | 41271 | 41271 | 41271 | 41271 | 41271 | 41271 | 41271 | 41271 |  | u8 | 1 | 0 | 0 | 0 | R
41272 | Smart Home ctrl syst 3 | Smart Home is controlling the system | 41272 | 41272 | 41272 | 41272 | 41272 | 41272 | 41272 | 41272 | 41272 | 41272 | 41272 | 41272 |  | u8 | 1 | 0 | 0 | 0 | R
41273 | Smart Home ctrl syst 2 | Smart Home is controlling the system | 41273 | 41273 | 41273 | 41273 | 41273 | 41273 | 41273 | 41273 | 41273 | 41273 | 41273 | 41273 |  | u8 | 1 | 0 | 0 | 0 | R
41274 | Smart Home ctrl syst 1 | Smart Home is controlling the system | 41274 | 41274 | 41274 | 41274 | 41274 | 41274 | 41274 | 41274 | 41274 | 41274 | 41274 | 41274 |  | u8 | 1 | 0 | 0 | 0 | R
41287 | OPT boiler has priority hot water | OPT boiler has priority hot water |  |  |  |  | 41287 | 41287 | 41287 | 41287 |  | 41287 | 41287 | 41287 |  | u8 | 1 | 0 | 0 | 0 | R
41393 | Smart energy source, energy source prio 7, start DM | Energy source prio 7, start DM |  |  |  |  | 41393 | 41393 | 41393 | 41393 |  | 41393 | 41393 | 41393 |  | s32 | 1 | 0 | 0 | 0 | R
41395 | Smart energy source, energy source prio 6, start DM | Energy source prio 6, start DM |  |  |  |  | 41395 | 41395 | 41395 | 41395 |  | 41395 | 41395 | 41395 |  | s32 | 1 | 0 | 0 | 0 | R
41397 | Smart energy source, energy source prio 5, start DM | Energy source prio 5, start DM |  |  |  |  | 41397 | 41397 | 41397 | 41397 |  | 41397 | 41397 | 41397 |  | s32 | 1 | 0 | 0 | 0 | R
41399 | Smart energy source, energy source prio 4, start DM | Energy source prio 4, start DM |  |  |  |  | 41399 | 41399 | 41399 | 41399 |  | 41399 | 41399 | 41399 |  | s32 | 1 | 0 | 0 | 0 | R
41401 | Smart energy source, energy source prio 3, start DM | Energy source prio 3, start DM |  |  |  |  | 41401 | 41401 | 41401 | 41401 |  | 41401 | 41401 | 41401 |  | s32 | 1 | 0 | 0 | 0 | R
41403 | Smart energy source, energy source prio 2, start DM | Energy source prio 2, start DM |  |  |  |  | 41403 | 41403 | 41403 | 41403 |  | 41403 | 41403 | 41403 |  | s32 | 1 | 0 | 0 | 0 | R
41405 | Smart energy source, energy source prio 1, start DM | Energy source prio 1, start DM |  |  |  |  | 41405 | 41405 | 41405 | 41405 |  | 41405 | 41405 | 41405 |  | s32 | 1 | 0 | 0 | 0 | R
41421 | Smart energy source, degree minute min value | Smart energy source, degree minute min value in Smart energy source system |  |  |  |  | 41421 | 41421 | 41421 | 41421 |  | 41421 | 41421 | 41421 |  | s32 | 1 | 0 | 0 | 0 | R
41424 | Smart energy source, actual OPT10 addition price | Smart energy source, actual OPT10 addition price. |  |  |  |  | 41424 | 41424 | 41424 | 41424 |  | 41424 | 41424 | 41424 |  | u16 | 1 | 0 | 0 | 0 | R
41425 | Smart energy source, actual shunt add price | Smart energy source, actual external step addition price. |  |  |  |  | 41425 | 41425 | 41425 | 41425 |  | 41425 | 41425 | 41425 |  | u16 | 1 | 0 | 0 | 0 | R
41426 | Smart energy source, actual ext. step add price | Smart energy source, actual external step add price. |  |  |  |  | 41426 | 41426 | 41426 | 41426 |  | 41426 | 41426 | 41426 |  | u16 | 1 | 0 | 0 | 0 | R
41427 | Smart energy source, actual electricity price | Smart energy source, actual electricity price. |  |  |  |  | 41427 | 41427 | 41427 | 41427 |  | 41427 | 41427 | 41427 |  | u16 | 1 | 0 | 0 | 0 | R
41429 | EP12-BT57 Collector In | [5 empty] | 41429 | 41429 | 41429 | 41429 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41430 | EP12-BT58 Collector Out | [5 empty] | 41430 | 41430 | 41430 | 41430 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41446 | Smart energy source prioritze OPT10 in hot water | [10 empty] | 41446 | 41446 | 41446 |  | u8 | 1 | 0 | 0 | 0 | R
41458 | wood boiler, 1= active, 0 = not active | [9 empty] | 41458 |  |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41468 | EB108 F2120 Alarm Number | [10 empty] | 41468 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41469 | EB108 F2120 Fan Speed | F2120 Current Fan Speed | [9 empty] | 41469 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41470 | EB108 F2120 Max Fan Speed | F2120 Current Max Fan Speed | [9 empty] | 41470 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41471 | EB108 F2120 Min Fan Speed | F2120 Current Min Fan Speed | [9 empty] | 41471 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41472 | EB108 F2120 Max Compressor Speed | F2120 Current Max Compressor Speed | [9 empty] | 41472 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41473 | EB108 F2120 Min Compressor Speed | F2120 Current Min Compressor Speed | [9 empty] | 41473 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41474 | EB108 F2120 Calculated Power | F2120 Current Calculated Power | [9 empty] | 41474 |  |  | kW | u16 | 10 | 0 | 0 | 0 | R
41475 | EB108 F2120 Time To Defrost | [10 empty] | 41475 |  |  | min | u16 | 1 | 0 | 0 | 0 | R
41493 | EB107 F2120 Alarm Number | [10 empty] | 41493 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41494 | EB107 F2120 Fan Speed | F2120 Current Fan Speed | [9 empty] | 41494 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41495 | EB107 F2120 Max Fan Speed | F2120 Current Max Fan Speed | [9 empty] | 41495 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41496 | EB107 F2120 Min Fan Speed | F2120 Current Min Fan Speed | [9 empty] | 41496 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41497 | EB107 F2120 Max Compressor Speed | F2120 Current Max Compressor Speed | [9 empty] | 41497 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41498 | EB107 F2120 Min Compressor Speed | F2120 Current Min Compressor Speed | [9 empty] | 41498 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41499 | EB107 F2120 Calculated Power | F2120 Current Calculated Power | [9 empty] | 41499 |  |  | kW | u16 | 10 | 0 | 0 | 0 | R
41500 | EB107 F2120 Time To Defrost | [10 empty] | 41500 |  |  | min | u16 | 1 | 0 | 0 | 0 | R
41518 | EB106 F2120 Alarm Number | [10 empty] | 41518 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41519 | EB106 F2120 Fan Speed | F2120 Current Fan Speed | [9 empty] | 41519 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41520 | EB106 F2120 Max Fan Speed | F2120 Current Max Fan Speed | [9 empty] | 41520 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41521 | EB106 F2120 Min Fan Speed | F2120 Current Min Fan Speed | [9 empty] | 41521 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41522 | EB106 F2120 Max Compressor Speed | F2120 Current Max Compressor Speed | [9 empty] | 41522 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41523 | EB106 F2120 Min Compressor Speed | F2120 Current Min Compressor Speed | [9 empty] | 41523 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41524 | EB106 F2120 Calculated Power | F2120 Current Calculated Power | [9 empty] | 41524 |  |  | kW | u16 | 10 | 0 | 0 | 0 | R
41525 | EB106 F2120 Time To Defrost | [10 empty] | 41525 |  |  | min | u16 | 1 | 0 | 0 | 0 | R
41543 | EB105 F2120 Alarm Number | [10 empty] | 41543 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41544 | EB105 F2120 Fan Speed | F2120 Current Fan Speed | [9 empty] | 41544 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41545 | EB105 F2120 Max Fan Speed | F2120 Current Max Fan Speed | [9 empty] | 41545 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41546 | EB105 F2120 Min Fan Speed | F2120 Current Min Fan Speed | [9 empty] | 41546 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41547 | EB105 F2120 Max Compressor Speed | F2120 Current Max Compressor Speed | [9 empty] | 41547 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41548 | EB105 F2120 Min Compressor Speed | F2120 Current Min Compressor Speed | [9 empty] | 41548 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41549 | EB105 F2120 Calculated Power | F2120 Current Calculated Power | [9 empty] | 41549 |  |  | kW | u16 | 10 | 0 | 0 | 0 | R
41550 | EB105 F2120 Time To Defrost | [10 empty] | 41550 |  |  | min | u16 | 1 | 0 | 0 | 0 | R
41568 | EB104 F2120 Alarm Number | [10 empty] | 41568 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41569 | EB104 F2120 Fan Speed | F2120 Current Fan Speed | [9 empty] | 41569 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41570 | EB104 F2120 Max Fan Speed | F2120 Current Max Fan Speed | [9 empty] | 41570 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41571 | EB104 F2120 Min Fan Speed | F2120 Current Min Fan Speed | [9 empty] | 41571 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41572 | EB104 F2120 Max Compressor Speed | F2120 Current Max Compressor Speed | [9 empty] | 41572 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41573 | EB104 F2120 Min Compressor Speed | F2120 Current Min Compressor Speed | [9 empty] | 41573 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41574 | EB104 F2120 Calculated Power | F2120 Current Calculated Power | [9 empty] | 41574 |  |  | kW | u16 | 10 | 0 | 0 | 0 | R
41575 | EB104 F2120 Time To Defrost | [10 empty] | 41575 |  |  | min | u16 | 1 | 0 | 0 | 0 | R
41593 | EB103 F2120 Alarm Number | [10 empty] | 41593 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41594 | EB103 F2120 Fan Speed | F2120 Current Fan Speed | [9 empty] | 41594 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41595 | EB103 F2120 Max Fan Speed | F2120 Current Max Fan Speed | [9 empty] | 41595 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41596 | EB103 F2120 Min Fan Speed | F2120 Current Min Fan Speed | [9 empty] | 41596 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41597 | EB103 F2120 Max Compressor Speed | F2120 Current Max Compressor Speed | [9 empty] | 41597 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41598 | EB103 F2120 Min Compressor Speed | F2120 Current Min Compressor Speed | [9 empty] | 41598 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41599 | EB103 F2120 Calculated Power | F2120 Current Calculated Power | [9 empty] | 41599 |  |  | kW | u16 | 10 | 0 | 0 | 0 | R
41600 | EB103 F2120 Time To Defrost | [10 empty] | 41600 |  |  | min | u16 | 1 | 0 | 0 | 0 | R
41618 | EB102 F2120 Alarm Number | [10 empty] | 41618 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
41619 | EB102 F2120 Fan Speed | F2120 Current Fan Speed | [9 empty] | 41619 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41620 | EB102 F2120 Max Fan Speed | F2120 Current Max Fan Speed | [9 empty] | 41620 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41621 | EB102 F2120 Min Fan Speed | F2120 Current Min Fan Speed | [9 empty] | 41621 |  |  | rpm | u16 | 1 | 0 | 0 | 0 | R
41622 | EB102 F2120 Max Compressor Speed | F2120 Current Max Compressor Speed | [9 empty] | 41622 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41623 | EB102 F2120 Min Compressor Speed | F2120 Current Min Compressor Speed | [9 empty] | 41623 |  |  | Hz | u16 | 10 | 0 | 0 | 0 | R
41624 | EB102 F2120 Calculated Power | F2120 Current Calculated Power | [9 empty] | 41624 |  |  | kW | u16 | 10 | 0 | 0 | 0 | R
41625 | EB102 F2120 Time To Defrost | [10 empty] | 41625 |  |  | min | u16 | 1 | 0 | 0 | 0 | R
41705 | Smart energy source prioritze in hot water | Smart energy source prioritze in hot water, 0 = Compressor, 1 = OPT10, 2 = Internal addition | [9 empty] | 41705 | 41705 | 41705 |  | u8 | 1 | 0 | 0 | 0 | R
41742 | EB108-EP15 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41742 | 41742 | 41742 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41743 | EB108-EP15 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41743 | 41743 | 41743 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41744 | EB108-EP14 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41744 | 41744 | 41744 |  | 41744 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41745 | EB108-EP14 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41745 | 41745 | 41745 |  | 41745 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41746 | EB107-EP15 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41746 | 41746 | 41746 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41747 | EB107-EP15 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41747 | 41747 | 41747 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41748 | EB107-EP14 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41748 | 41748 | 41748 |  | 41748 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41749 | EB107-EP14 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41749 | 41749 | 41749 |  | 41749 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41750 | EB106-EP15 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41750 | 41750 | 41750 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41751 | EB106-EP15 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41751 | 41751 | 41751 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41752 | EB106-EP14 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41752 | 41752 | 41752 |  | 41752 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41753 | EB106-EP14 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41753 | 41753 | 41753 |  | 41753 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41754 | EB105-EP15 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41754 | 41754 | 41754 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41755 | EB105-EP15 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41755 | 41755 | 41755 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41756 | EB105-EP14 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41756 | 41756 | 41756 |  | 41756 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41757 | EB105-EP14 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41757 | 41757 | 41757 |  | 41757 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41758 | EB104-EP15 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41758 | 41758 | 41758 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41759 | EB104-EP15 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41759 | 41759 | 41759 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41760 | EB104-EP14 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41760 | 41760 | 41760 |  | 41760 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41761 | EB104-EP14 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41761 | 41761 | 41761 |  | 41761 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41762 | EB103-EP15 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41762 | 41762 | 41762 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41763 | EB103-EP15 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41763 | 41763 | 41763 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41764 | EB103-EP14 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41764 | 41764 | 41764 |  | 41764 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41765 | EB103-EP14 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41765 | 41765 | 41765 |  | 41765 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41766 | EB102-EP15 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41766 | 41766 | 41766 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41767 | EB102-EP15 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41767 | 41767 | 41767 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41768 | EB102-EP14 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41768 | 41768 | 41768 |  | 41768 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41769 | EB102-EP14 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41769 | 41769 | 41769 |  | 41769 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41770 | EB101-EP15 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41770 | 41770 | 41770 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41771 | EB101-EP15 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41771 | 41771 | 41771 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
41772 | EB101-EP14 Alarm condensor in level | Alarm condensor in level | [5 empty] | 41772 | 41772 | 41772 | 41772 | 41772 | 41772 | 41772 | °C | s16 | 10 | 0 | 0 | 0 | R
41773 | EB101-EP14 Alarm condensor out level | Alarm condensor out level | [5 empty] | 41773 | 41773 | 41773 | 41773 | 41773 | 41773 | 41773 | °C | s16 | 10 | 0 | 0 | 0 | R
41787 | EB100-BL3 Condensation water level guard |  |  |  |  | 41787 | [9 empty] | s16 | 1 | 0 | 0 | 0 | R
41789 | EB108 Compressor EP15 size | [7 empty] | 41789 | 41789 |  |  |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
41793 | EB107 Compressor EP15 size | [7 empty] | 41793 | 41793 |  |  |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
41797 | EB106 Compressor EP15 size | [7 empty] | 41797 | 41797 |  |  |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
41801 | EB105 Compressor EP15 size | [7 empty] | 41801 | 41801 |  |  |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
41805 | EB104 Compressor EP15 size | [7 empty] | 41805 | 41805 |  |  |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
41809 | EB103 Compressor EP15 size | [7 empty] | 41809 | 41809 |  |  |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
41813 | EB102 Compressor EP15 size | [7 empty] | 41813 | 41813 |  |  |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
41817 | EB101 Compressor EP15 size | [7 empty] | 41817 | 41817 |  |  |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
41846 | HP consumed energy due to ventilation |  |  |  |  | 41846 | [8 empty] | kWh | u32 | 10 | 0 | 2147483647 | 0 | R
41848 | HP consumed energy due to hot water |  |  |  |  | 41848 | [8 empty] | kWh | u32 | 10 | 0 | 2147483647 | 0 | R
41850 | HP consumed energy due to heating |  |  |  |  | 41850 | [8 empty] | kWh | u32 | 10 | 0 | 2147483647 | 0 | R
41862 | EB108-EP15 set point for BT12 | set point for BT12 | [6 empty] | 41862 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41863 | EB108-EP15 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41863 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41864 | EB108-EP14 set point for BT12 | set point for BT12 | [6 empty] | 41864 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41865 | EB108-EP14 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41865 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41866 | EB107-EP15 set point for BT12 | set point for BT12 | [6 empty] | 41866 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41867 | EB107-EP15 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41867 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41868 | EB107-EP14 set point for BT12 | set point for BT12 | [6 empty] | 41868 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41869 | EB107-EP14 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41869 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41870 | EB106-EP15 set point for BT12 | set point for BT12 | [6 empty] | 41870 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41871 | EB106-EP15 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41871 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41872 | EB106-EP14 set point for BT12 | set point for BT12 | [6 empty] | 41872 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41873 | EB106-EP14 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41873 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41874 | EB105-EP15 set point for BT12 | set point for BT12 | [6 empty] | 41874 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41875 | EB105-EP15 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41875 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41876 | EB105-EP14 set point for BT12 | set point for BT12 | [6 empty] | 41876 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41877 | EB105-EP14 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41877 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41878 | EB104-EP15 set point for BT12 | set point for BT12 | [6 empty] | 41878 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41879 | EB104-EP15 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41879 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41880 | EB104-EP14 set point for BT12 | set point for BT12 | [6 empty] | 41880 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41881 | EB104-EP14 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41881 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41882 | EB103-EP15 set point for BT12 | set point for BT12 | [6 empty] | 41882 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41883 | EB103-EP15 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41883 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41884 | EB103-EP14 set point for BT12 | set point for BT12 | [6 empty] | 41884 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41885 | EB103-EP14 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41885 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41886 | EB102-EP15 set point for BT12 | set point for BT12 | [6 empty] | 41886 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41887 | EB102-EP15 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41887 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41888 | EB102-EP14 set point for BT12 | set point for BT12 | [6 empty] | 41888 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41889 | EB102-EP14 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41889 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41890 | EB101-EP15 set point for BT12 | set point for BT12 | [6 empty] | 41890 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41891 | EB101-EP15 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41891 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41892 | EB101-EP14 set point for BT12 | set point for BT12 | [6 empty] | 41892 | [5 empty] | °C | s16 | 1 | 0 | 0 | 0 | R
41893 | EB101-EP14 start up frequency for inverter module | start up frequency in heating for inverter module | [6 empty] | 41893 | [5 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R
41928 | Smart Price Adaption Price | The current electric price | 41928 | 41928 | 41928 | 41928 | 41928 | 41928 | 41928 | 41928 | 41928 | 41928 | 41928 | 41928 |  | u16 | 100 | 0 | 0 | 0 | R
41929 | Smart Price Adaption Price Level | Whether the current price is unknown (0), low (1), medium (2), high (3) | 41929 | 41929 | 41929 | 41929 | 41929 | 41929 | 41929 | 41929 | 41929 | 41929 | 41929 | 41929 |  | u8 | 1 | 0 | 0 | 0 | R
41930 | AA23-BE5 Power 10 |  | 41930 | 41930 | 41930 | 41930 | 41930 | 41930 | 41930 | 41930 | 41930 | 41930 | 41930 | 41930 | W | u16 | 1 | 0 | 0 | 0 | R
41931 | AA23-BE5 Power 9 |  | 41931 | 41931 | 41931 | 41931 | 41931 | 41931 | 41931 | 41931 | 41931 | 41931 | 41931 | 41931 | W | u16 | 1 | 0 | 0 | 0 | R
41932 | AA23-BE5 Power 8 |  | 41932 | 41932 | 41932 | 41932 | 41932 | 41932 | 41932 | 41932 | 41932 | 41932 | 41932 | 41932 | W | u16 | 1 | 0 | 0 | 0 | R
41933 | AA23-BE5 Power 7 |  | 41933 | 41933 | 41933 | 41933 | 41933 | 41933 | 41933 | 41933 | 41933 | 41933 | 41933 | 41933 | W | u16 | 1 | 0 | 0 | 0 | R
41934 | AA23-BE5 Power 6 |  | 41934 | 41934 | 41934 | 41934 | 41934 | 41934 | 41934 | 41934 | 41934 | 41934 | 41934 | 41934 | W | u16 | 1 | 0 | 0 | 0 | R
41935 | AA23-BE5 Power 5 |  | 41935 | 41935 | 41935 | 41935 | 41935 | 41935 | 41935 | 41935 | 41935 | 41935 | 41935 | 41935 | W | u16 | 1 | 0 | 0 | 0 | R
41936 | AA23-BE5 Power 4 |  | 41936 | 41936 | 41936 | 41936 | 41936 | 41936 | 41936 | 41936 | 41936 | 41936 | 41936 | 41936 | W | u16 | 1 | 0 | 0 | 0 | R
41937 | AA23-BE5 Power 3 |  | 41937 | 41937 | 41937 | 41937 | 41937 | 41937 | 41937 | 41937 | 41937 | 41937 | 41937 | 41937 | W | u16 | 1 | 0 | 0 | 0 | R
41938 | AA23-BE5 Power 2 |  | 41938 | 41938 | 41938 | 41938 | 41938 | 41938 | 41938 | 41938 | 41938 | 41938 | 41938 | 41938 | W | u16 | 1 | 0 | 0 | 0 | R
41939 | AA23-BE5 Power 1 |  | 41939 | 41939 | 41939 | 41939 | 41939 | 41939 | 41939 | 41939 | 41939 | 41939 | 41939 | 41939 | W | u16 | 1 | 0 | 0 | 0 | R
41940 | AA23-BE5 Error High 10 |  | 41940 | 41940 | 41940 | 41940 | 41940 | 41940 | 41940 | 41940 | 41940 | 41940 | 41940 | 41940 | W | u16 | 1 | 0 | 0 | 0 | R
41941 | AA23-BE5 Error High 9 |  | 41941 | 41941 | 41941 | 41941 | 41941 | 41941 | 41941 | 41941 | 41941 | 41941 | 41941 | 41941 | W | u16 | 1 | 0 | 0 | 0 | R
41942 | AA23-BE5 Error High 8 |  | 41942 | 41942 | 41942 | 41942 | 41942 | 41942 | 41942 | 41942 | 41942 | 41942 | 41942 | 41942 | W | u16 | 1 | 0 | 0 | 0 | R
41943 | AA23-BE5 Error High 7 |  | 41943 | 41943 | 41943 | 41943 | 41943 | 41943 | 41943 | 41943 | 41943 | 41943 | 41943 | 41943 | W | u16 | 1 | 0 | 0 | 0 | R
41944 | AA23-BE5 Error High 6 |  | 41944 | 41944 | 41944 | 41944 | 41944 | 41944 | 41944 | 41944 | 41944 | 41944 | 41944 | 41944 | W | u16 | 1 | 0 | 0 | 0 | R
41945 | AA23-BE5 Error High 5 |  | 41945 | 41945 | 41945 | 41945 | 41945 | 41945 | 41945 | 41945 | 41945 | 41945 | 41945 | 41945 | W | u16 | 1 | 0 | 0 | 0 | R
41946 | AA23-BE5 Error High 4 |  | 41946 | 41946 | 41946 | 41946 | 41946 | 41946 | 41946 | 41946 | 41946 | 41946 | 41946 | 41946 | W | u16 | 1 | 0 | 0 | 0 | R
41947 | AA23-BE5 Error High 3 |  | 41947 | 41947 | 41947 | 41947 | 41947 | 41947 | 41947 | 41947 | 41947 | 41947 | 41947 | 41947 | W | u16 | 1 | 0 | 0 | 0 | R
41948 | AA23-BE5 Error High 2 |  | 41948 | 41948 | 41948 | 41948 | 41948 | 41948 | 41948 | 41948 | 41948 | 41948 | 41948 | 41948 | W | u16 | 1 | 0 | 0 | 0 | R
41949 | AA23-BE5 Error High 1 |  | 41949 | 41949 | 41949 | 41949 | 41949 | 41949 | 41949 | 41949 | 41949 | 41949 | 41949 | 41949 | W | u16 | 1 | 0 | 0 | 0 | R
41950 | AA23-BE5 Error Low 10 |  | 41950 | 41950 | 41950 | 41950 | 41950 | 41950 | 41950 | 41950 | 41950 | 41950 | 41950 | 41950 | W | u16 | 1 | 0 | 0 | 0 | R
41951 | AA23-BE5 Error Low 9 |  | 41951 | 41951 | 41951 | 41951 | 41951 | 41951 | 41951 | 41951 | 41951 | 41951 | 41951 | 41951 | W | u16 | 1 | 0 | 0 | 0 | R
41952 | AA23-BE5 Error Low 8 |  | 41952 | 41952 | 41952 | 41952 | 41952 | 41952 | 41952 | 41952 | 41952 | 41952 | 41952 | 41952 | W | u16 | 1 | 0 | 0 | 0 | R
41953 | AA23-BE5 Error Low 7 |  | 41953 | 41953 | 41953 | 41953 | 41953 | 41953 | 41953 | 41953 | 41953 | 41953 | 41953 | 41953 | W | u16 | 1 | 0 | 0 | 0 | R
41954 | AA23-BE5 Error Low 6 |  | 41954 | 41954 | 41954 | 41954 | 41954 | 41954 | 41954 | 41954 | 41954 | 41954 | 41954 | 41954 | W | u16 | 1 | 0 | 0 | 0 | R
41955 | AA23-BE5 Error Low 5 |  | 41955 | 41955 | 41955 | 41955 | 41955 | 41955 | 41955 | 41955 | 41955 | 41955 | 41955 | 41955 | W | u16 | 1 | 0 | 0 | 0 | R
41956 | AA23-BE5 Error Low 4 |  | 41956 | 41956 | 41956 | 41956 | 41956 | 41956 | 41956 | 41956 | 41956 | 41956 | 41956 | 41956 | W | u16 | 1 | 0 | 0 | 0 | R
41957 | AA23-BE5 Error Low 3 |  | 41957 | 41957 | 41957 | 41957 | 41957 | 41957 | 41957 | 41957 | 41957 | 41957 | 41957 | 41957 | W | u16 | 1 | 0 | 0 | 0 | R
41958 | AA23-BE5 Error Low 2 |  | 41958 | 41958 | 41958 | 41958 | 41958 | 41958 | 41958 | 41958 | 41958 | 41958 | 41958 | 41958 | W | u16 | 1 | 0 | 0 | 0 | R
41959 | AA23-BE5 Error Low 1 |  | 41959 | 41959 | 41959 | 41959 | 41959 | 41959 | 41959 | 41959 | 41959 | 41959 | 41959 | 41959 | W | u16 | 1 | 0 | 0 | 0 | R
41960 | AA23-BE5 Com Percentage 10 |  | 41960 | 41960 | 41960 | 41960 | 41960 | 41960 | 41960 | 41960 | 41960 | 41960 | 41960 | 41960 | % | u8 | 1 | 0 | 0 | 0 | R
41961 | AA23-BE5 Com Percentage 9 |  | 41961 | 41961 | 41961 | 41961 | 41961 | 41961 | 41961 | 41961 | 41961 | 41961 | 41961 | 41961 | % | u8 | 1 | 0 | 0 | 0 | R
41962 | AA23-BE5 Com Percentage 8 |  | 41962 | 41962 | 41962 | 41962 | 41962 | 41962 | 41962 | 41962 | 41962 | 41962 | 41962 | 41962 | % | u8 | 1 | 0 | 0 | 0 | R
41963 | AA23-BE5 Com Percentage 7 |  | 41963 | 41963 | 41963 | 41963 | 41963 | 41963 | 41963 | 41963 | 41963 | 41963 | 41963 | 41963 | % | u8 | 1 | 0 | 0 | 0 | R
41964 | AA23-BE5 Com Percentage 6 |  | 41964 | 41964 | 41964 | 41964 | 41964 | 41964 | 41964 | 41964 | 41964 | 41964 | 41964 | 41964 | % | u8 | 1 | 0 | 0 | 0 | R
41965 | AA23-BE5 Com Percentage 5 |  | 41965 | 41965 | 41965 | 41965 | 41965 | 41965 | 41965 | 41965 | 41965 | 41965 | 41965 | 41965 | % | u8 | 1 | 0 | 0 | 0 | R
41966 | AA23-BE5 Com Percentage 4 |  | 41966 | 41966 | 41966 | 41966 | 41966 | 41966 | 41966 | 41966 | 41966 | 41966 | 41966 | 41966 | % | u8 | 1 | 0 | 0 | 0 | R
41967 | AA23-BE5 Com Percentage 3 |  | 41967 | 41967 | 41967 | 41967 | 41967 | 41967 | 41967 | 41967 | 41967 | 41967 | 41967 | 41967 | % | u8 | 1 | 0 | 0 | 0 | R
41968 | AA23-BE5 Com Percentage 2 |  | 41968 | 41968 | 41968 | 41968 | 41968 | 41968 | 41968 | 41968 | 41968 | 41968 | 41968 | 41968 | % | u8 | 1 | 0 | 0 | 0 | R
41969 | AA23-BE5 Com Percentage 1 |  | 41969 | 41969 | 41969 | 41969 | 41969 | 41969 | 41969 | 41969 | 41969 | 41969 | 41969 | 41969 | % | u8 | 1 | 0 | 0 | 0 | R
41980 | AA23-BE5 Voltage1 10 |  | 41980 | 41980 | 41980 | 41980 | 41980 | 41980 | 41980 | 41980 | 41980 | 41980 | 41980 | 41980 | V | u16 | 10 | 0 | 0 | 0 | R
41981 | AA23-BE5 Voltage1 9 |  | 41981 | 41981 | 41981 | 41981 | 41981 | 41981 | 41981 | 41981 | 41981 | 41981 | 41981 | 41981 | V | u16 | 10 | 0 | 0 | 0 | R
41982 | AA23-BE5 Voltage1 8 |  | 41982 | 41982 | 41982 | 41982 | 41982 | 41982 | 41982 | 41982 | 41982 | 41982 | 41982 | 41982 | V | u16 | 10 | 0 | 0 | 0 | R
41983 | AA23-BE5 Voltage1 7 |  | 41983 | 41983 | 41983 | 41983 | 41983 | 41983 | 41983 | 41983 | 41983 | 41983 | 41983 | 41983 | V | u16 | 10 | 0 | 0 | 0 | R
41984 | AA23-BE5 Voltage1 6 |  | 41984 | 41984 | 41984 | 41984 | 41984 | 41984 | 41984 | 41984 | 41984 | 41984 | 41984 | 41984 | V | u16 | 10 | 0 | 0 | 0 | R
41985 | AA23-BE5 Voltage1 5 |  | 41985 | 41985 | 41985 | 41985 | 41985 | 41985 | 41985 | 41985 | 41985 | 41985 | 41985 | 41985 | V | u16 | 10 | 0 | 0 | 0 | R
41986 | AA23-BE5 Voltage1 4 |  | 41986 | 41986 | 41986 | 41986 | 41986 | 41986 | 41986 | 41986 | 41986 | 41986 | 41986 | 41986 | V | u16 | 10 | 0 | 0 | 0 | R
41987 | AA23-BE5 Voltage1 3 |  | 41987 | 41987 | 41987 | 41987 | 41987 | 41987 | 41987 | 41987 | 41987 | 41987 | 41987 | 41987 | V | u16 | 10 | 0 | 0 | 0 | R
41988 | AA23-BE5 Voltage1 2 |  | 41988 | 41988 | 41988 | 41988 | 41988 | 41988 | 41988 | 41988 | 41988 | 41988 | 41988 | 41988 | V | u16 | 10 | 0 | 0 | 0 | R
41989 | AA23-BE5 Voltage1 1 |  | 41989 | 41989 | 41989 | 41989 | 41989 | 41989 | 41989 | 41989 | 41989 | 41989 | 41989 | 41989 | V | u16 | 10 | 0 | 0 | 0 | R
41990 | AA23-BE5 Voltage2 10 |  | 41990 | 41990 | 41990 | 41990 | 41990 | 41990 | 41990 | 41990 | 41990 | 41990 | 41990 | 41990 | V | u16 | 10 | 0 | 0 | 0 | R
41991 | AA23-BE5 Voltage2 9 |  | 41991 | 41991 | 41991 | 41991 | 41991 | 41991 | 41991 | 41991 | 41991 | 41991 | 41991 | 41991 | V | u16 | 10 | 0 | 0 | 0 | R
41992 | AA23-BE5 Voltage2 8 |  | 41992 | 41992 | 41992 | 41992 | 41992 | 41992 | 41992 | 41992 | 41992 | 41992 | 41992 | 41992 | V | u16 | 10 | 0 | 0 | 0 | R
41993 | AA23-BE5 Voltage2 7 |  | 41993 | 41993 | 41993 | 41993 | 41993 | 41993 | 41993 | 41993 | 41993 | 41993 | 41993 | 41993 | V | u16 | 10 | 0 | 0 | 0 | R
41994 | AA23-BE5 Voltage2 6 |  | 41994 | 41994 | 41994 | 41994 | 41994 | 41994 | 41994 | 41994 | 41994 | 41994 | 41994 | 41994 | V | u16 | 10 | 0 | 0 | 0 | R
41995 | AA23-BE5 Voltage2 5 |  | 41995 | 41995 | 41995 | 41995 | 41995 | 41995 | 41995 | 41995 | 41995 | 41995 | 41995 | 41995 | V | u16 | 10 | 0 | 0 | 0 | R
41996 | AA23-BE5 Voltage2 4 |  | 41996 | 41996 | 41996 | 41996 | 41996 | 41996 | 41996 | 41996 | 41996 | 41996 | 41996 | 41996 | V | u16 | 10 | 0 | 0 | 0 | R
41997 | AA23-BE5 Voltage2 3 |  | 41997 | 41997 | 41997 | 41997 | 41997 | 41997 | 41997 | 41997 | 41997 | 41997 | 41997 | 41997 | V | u16 | 10 | 0 | 0 | 0 | R
41998 | AA23-BE5 Voltage2 2 |  | 41998 | 41998 | 41998 | 41998 | 41998 | 41998 | 41998 | 41998 | 41998 | 41998 | 41998 | 41998 | V | u16 | 10 | 0 | 0 | 0 | R
41999 | AA23-BE5 Voltage2 1 |  | 41999 | 41999 | 41999 | 41999 | 41999 | 41999 | 41999 | 41999 | 41999 | 41999 | 41999 | 41999 | V | u16 | 10 | 0 | 0 | 0 | R
42000 | AA23-BE5 Temperature 10 |  | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | °C | u16 | 10 | 0 | 0 | 0 | R
42001 | AA23-BE5 Temperature 9 |  | 42001 | 42001 | 42001 | 42001 | 42001 | 42001 | 42001 | 42001 | 42001 | 42001 | 42001 | 42001 | °C | u16 | 10 | 0 | 0 | 0 | R
42002 | AA23-BE5 Temperature 8 |  | 42002 | 42002 | 42002 | 42002 | 42002 | 42002 | 42002 | 42002 | 42002 | 42002 | 42002 | 42002 | °C | u16 | 10 | 0 | 0 | 0 | R
42003 | AA23-BE5 Temperature 7 |  | 42003 | 42003 | 42003 | 42003 | 42003 | 42003 | 42003 | 42003 | 42003 | 42003 | 42003 | 42003 | °C | u16 | 10 | 0 | 0 | 0 | R
42004 | AA23-BE5 Temperature 6 |  | 42004 | 42004 | 42004 | 42004 | 42004 | 42004 | 42004 | 42004 | 42004 | 42004 | 42004 | 42004 | °C | u16 | 10 | 0 | 0 | 0 | R
42005 | AA23-BE5 Temperature 5 |  | 42005 | 42005 | 42005 | 42005 | 42005 | 42005 | 42005 | 42005 | 42005 | 42005 | 42005 | 42005 | °C | u16 | 10 | 0 | 0 | 0 | R
42006 | AA23-BE5 Temperature 4 |  | 42006 | 42006 | 42006 | 42006 | 42006 | 42006 | 42006 | 42006 | 42006 | 42006 | 42006 | 42006 | °C | u16 | 10 | 0 | 0 | 0 | R
42007 | AA23-BE5 Temperature 3 |  | 42007 | 42007 | 42007 | 42007 | 42007 | 42007 | 42007 | 42007 | 42007 | 42007 | 42007 | 42007 | °C | u16 | 10 | 0 | 0 | 0 | R
42008 | AA23-BE5 Temperature 2 |  | 42008 | 42008 | 42008 | 42008 | 42008 | 42008 | 42008 | 42008 | 42008 | 42008 | 42008 | 42008 | °C | u16 | 10 | 0 | 0 | 0 | R
42009 | AA23-BE5 Temperature 1 |  | 42009 | 42009 | 42009 | 42009 | 42009 | 42009 | 42009 | 42009 | 42009 | 42009 | 42009 | 42009 | °C | u16 | 10 | 0 | 0 | 0 | R
42010 | AA23-BE5 Energy 10 |  | 42010 | 42010 | 42010 | 42010 | 42010 | 42010 | 42010 | 42010 | 42010 | 42010 | 42010 | 42010 | kWh | u32 | 10 | 0 | 0 | 0 | R
42012 | AA23-BE5 Energy 9 |  | 42012 | 42012 | 42012 | 42012 | 42012 | 42012 | 42012 | 42012 | 42012 | 42012 | 42012 | 42012 | kWh | u32 | 10 | 0 | 0 | 0 | R
42014 | AA23-BE5 Energy 8 |  | 42014 | 42014 | 42014 | 42014 | 42014 | 42014 | 42014 | 42014 | 42014 | 42014 | 42014 | 42014 | kWh | u32 | 10 | 0 | 0 | 0 | R
42016 | AA23-BE5 Energy 7 |  | 42016 | 42016 | 42016 | 42016 | 42016 | 42016 | 42016 | 42016 | 42016 | 42016 | 42016 | 42016 | kWh | u32 | 10 | 0 | 0 | 0 | R
42018 | AA23-BE5 Energy 6 |  | 42018 | 42018 | 42018 | 42018 | 42018 | 42018 | 42018 | 42018 | 42018 | 42018 | 42018 | 42018 | kWh | u32 | 10 | 0 | 0 | 0 | R
42020 | AA23-BE5 Energy 5 |  | 42020 | 42020 | 42020 | 42020 | 42020 | 42020 | 42020 | 42020 | 42020 | 42020 | 42020 | 42020 | kWh | u32 | 10 | 0 | 0 | 0 | R
42022 | AA23-BE5 Energy 4 |  | 42022 | 42022 | 42022 | 42022 | 42022 | 42022 | 42022 | 42022 | 42022 | 42022 | 42022 | 42022 | kWh | u32 | 10 | 0 | 0 | 0 | R
42024 | AA23-BE5 Energy 3 |  | 42024 | 42024 | 42024 | 42024 | 42024 | 42024 | 42024 | 42024 | 42024 | 42024 | 42024 | 42024 | kWh | u32 | 10 | 0 | 0 | 0 | R
42026 | AA23-BE5 Energy 2 |  | 42026 | 42026 | 42026 | 42026 | 42026 | 42026 | 42026 | 42026 | 42026 | 42026 | 42026 | 42026 | kWh | u32 | 10 | 0 | 0 | 0 | R
42028 | AA23-BE5 Energy 1 |  | 42028 | 42028 | 42028 | 42028 | 42028 | 42028 | 42028 | 42028 | 42028 | 42028 | 42028 | 42028 | kWh | u32 | 10 | 0 | 0 | 0 | R
42030 | AA23-BE5 EME20 Version |  | 42030 | 42030 | 42030 | 42030 | 42030 | 42030 | 42030 | 42030 | 42030 | 42030 | 42030 | 42030 |  | u16 | 1 | 0 | 0 | 0 | R
42033 | PV Panel Heat Offset |  | 42033 | 42033 | 42033 | 42033 | 42033 | 42033 | 42033 | 42033 | 42033 | 42033 | 42033 | 42033 | °C | u8 | 10 | 0 | 0 | 0 | R
42034 | PV Panel Pool Offset |  | 42034 | 42034 | 42034 | 42034 | 42034 | 42034 | 42034 | 42034 |  | 42034 | 42034 | 42034 | °C | u8 | 10 | 0 | 0 | 0 | R
42035 | AA23-BE5 EME20 Total Power |  | 42035 | 42035 | 42035 | 42035 | 42035 | 42035 | 42035 | 42035 | 42035 | 42035 | 42035 | 42035 | W | u32 | 1 | 0 | 0 | 0 | R
42037 | AA23-BE5 EME20 Total Average Power |  | 42037 | 42037 | 42037 | 42037 | 42037 | 42037 | 42037 | 42037 | 42037 | 42037 | 42037 | 42037 | W | u32 | 1 | 0 | 0 | 0 | R
42075 | AA23-BE5 EME20 Total Energy |  | 42075 | 42075 | 42075 | 42075 | 42075 | 42075 | 42075 | 42075 | 42075 | 42075 | 42075 | 42075 | kWh | u32 | 10 | 0 | 0 | 0 | R
42080 | AA23-BE5 Alarm 504 |  | 42080 | 42080 | 42080 | 42080 | 42080 | 42080 | 42080 | 42080 | 42080 | 42080 | 42080 | 42080 |  | u8 | 1 | 0 | 0 | 0 | R
42081 | AA23-BE5 Alarm 505 |  | 42081 | 42081 | 42081 | 42081 | 42081 | 42081 | 42081 | 42081 | 42081 | 42081 | 42081 | 42081 |  | u8 | 1 | 0 | 0 | 0 | R
42082 | AA23-BE5 Alarm 506 |  | 42082 | 42082 | 42082 | 42082 | 42082 | 42082 | 42082 | 42082 | 42082 | 42082 | 42082 | 42082 |  | u8 | 1 | 0 | 0 | 0 | R
42083 | AA23-BE5 Alarm 507 |  | 42083 | 42083 | 42083 | 42083 | 42083 | 42083 | 42083 | 42083 | 42083 | 42083 | 42083 | 42083 |  | u8 | 1 | 0 | 0 | 0 | R
42084 | AA23-BE5 Alarm 508 |  | 42084 | 42084 | 42084 | 42084 | 42084 | 42084 | 42084 | 42084 | 42084 | 42084 | 42084 | 42084 |  | u8 | 1 | 0 | 0 | 0 | R
42085 | AA23-BE5 Alarm 509 |  | 42085 | 42085 | 42085 | 42085 | 42085 | 42085 | 42085 | 42085 | 42085 | 42085 | 42085 | 42085 |  | u8 | 1 | 0 | 0 | 0 | R
42086 | AA23-BE5 Alarm 510 |  | 42086 | 42086 | 42086 | 42086 | 42086 | 42086 | 42086 | 42086 | 42086 | 42086 | 42086 | 42086 |  | u8 | 1 | 0 | 0 | 0 | R
42087 | AA23-BE5 Alarm 511 |  | 42087 | 42087 | 42087 | 42087 | 42087 | 42087 | 42087 | 42087 | 42087 | 42087 | 42087 | 42087 |  | u8 | 1 | 0 | 0 | 0 | R
42093 | External SAM accessory GQ3 speed | Indicates the speed of the GQ3 fan speed in the SAM accessory. |  |  | 42093 | [9 empty] | % | u8 | 1 | 0 | 0 | 0 | R
42097 | Ground water pump auto speed | Ground water pump auto speed |  |  |  |  | 42097 | 42097 | 42097 | 42097 | [5 empty] | s8 | 1 | 0 | 0 | 0 | R/W
42100 | BT1 Average, 24h | EB100-BT1 Outdoor temperature average, 24h | 42100 | 42100 | 42100 | 42100 | 42100 | 42100 | 42100 | 42100 | 42100 | 42100 | 42100 | 42100 | °C | s16 | 10 | 0 | 0 | 0 | R
42101 | Used heating power average, 24h | Used heating power average, 24h | 42101 | 42101 | 42101 | 42101 | 42101 | 42101 | 42101 | 42101 | 42101 | 42101 | 42101 | 42101 | °C | s16 | 10 | 0 | 0 | 0 | R
42136 | BT22 Supply air temp. | [8 empty] | 42136 |  | 42136 | 42136 | 42136 | °C | s16 | 10 | 0 | 0 | 0 | R
42137 | BT22 Supply air temp. | [8 empty] | 42137 |  | 42137 | 42137 | 42137 | °C | s16 | 10 | 0 | 0 | 0 | R
42138 | BT22 Supply air temp. | [8 empty] | 42138 |  | 42138 | 42138 | 42138 | °C | s16 | 10 | 0 | 0 | 0 | R
42139 | AZ30-BT23 Outdoor temp. ERS 4 | [5 empty] | 42139 | 42139 | 42139 | 42139 |  | 42139 | 42139 | 42139 | °C | s16 | 10 | 0 | 0 | 0 | R
42140 | AZ30-BT23 Outdoor temp. ERS 3 | [5 empty] | 42140 | 42140 | 42140 | 42140 |  | 42140 | 42140 | 42140 | °C | s16 | 10 | 0 | 0 | 0 | R
42141 | AZ30-BT23 Outdoor temp. ERS 2 | [5 empty] | 42141 | 42141 | 42141 | 42141 |  | 42141 | 42141 | 42141 | °C | s16 | 10 | 0 | 0 | 0 | R
42150 | External ERS 4 accessory relays | Indicates the status of the relays on the ERS accessory. The information is binary encoded. b0: K1, b1: K2, b2: K3, b3: K4 |  |  |  |  | 42150 | 42150 | 42150 | 42150 |  | 42150 | 42150 | 42150 |  | u8 | 1 | 0 | 0 | 0 | R
42151 | External ERS 3 accessory relays | Indicates the status of the relays on the ERS accessory. The information is binary encoded. b0: K1, b1: K2, b2: K3, b3: K4 |  |  |  |  | 42151 | 42151 | 42151 | 42151 |  | 42151 | 42151 | 42151 |  | u8 | 1 | 0 | 0 | 0 | R
42152 | External ERS 2 accessory relays | Indicates the status of the relays on the ERS accessory. The information is binary encoded. b0: K1, b1: K2, b2: K3, b3: K4 |  |  |  |  | 42152 | 42152 | 42152 | 42152 |  | 42152 | 42152 | 42152 |  | u8 | 1 | 0 | 0 | 0 | R
42153 | External ERS 4 accessory GQ2 speed | Indicates the speed of the GQ2 fan speed on the ERS accessory. |  |  |  |  | 42153 | 42153 | 42153 | 42153 |  | 42153 | 42153 | 42153 | % | u8 | 1 | 0 | 0 | 0 | R
42154 | External ERS 3 accessory GQ2 speed | Indicates the speed of the GQ2 fan speed on the ERS accessory. |  |  |  |  | 42154 | 42154 | 42154 | 42154 |  | 42154 | 42154 | 42154 | % | u8 | 1 | 0 | 0 | 0 | R
42155 | External ERS 2 accessory GQ2 speed | Indicates the speed of the GQ2 fan speed on the ERS accessory. |  |  |  |  | 42155 | 42155 | 42155 | 42155 |  | 42155 | 42155 | 42155 | % | u8 | 1 | 0 | 0 | 0 | R
42156 | External ERS 4 accessory GQ3 speed | Indicates the speed of the GQ3 fan speed on the ERS accessory. |  |  |  |  | 42156 | 42156 | 42156 | 42156 |  | 42156 | 42156 | 42156 | % | u8 | 1 | 0 | 0 | 0 | R
42157 | External ERS 3 accessory GQ3 speed | Indicates the speed of the GQ3 fan speed on the ERS accessory. |  |  |  |  | 42157 | 42157 | 42157 | 42157 |  | 42157 | 42157 | 42157 | % | u8 | 1 | 0 | 0 | 0 | R
42158 | External ERS 2 accessory GQ3 speed | Indicates the speed of the GQ3 fan speed on the ERS accessory. |  |  |  |  | 42158 | 42158 | 42158 | 42158 |  | 42158 | 42158 | 42158 | % | u8 | 1 | 0 | 0 | 0 | R
42159 | External ERS 4 accessory block status | Indicates if the ERS accessory is externaly blocked. |  |  |  |  | 42159 | 42159 | 42159 | 42159 |  | 42159 | 42159 | 42159 |  | u8 | 1 | 0 | 0 | 0 | R
42160 | External ERS 3 accessory block status | Indicates if the ERS accessory is externaly blocked. |  |  |  |  | 42160 | 42160 | 42160 | 42160 |  | 42160 | 42160 | 42160 |  | u8 | 1 | 0 | 0 | 0 | R
42161 | External ERS 2 accessory block status | Indicates if the ERS accessory is externaly blocked. |  |  |  |  | 42161 | 42161 | 42161 | 42161 |  | 42161 | 42161 | 42161 |  | u8 | 1 | 0 | 0 | 0 | R
42162 | External ERS 4 accessory EB17 | Indicates if the status of ERS accessory EB17. I = closed, 0 = open. |  |  |  |  | 42162 | 42162 | 42162 | 42162 |  | 42162 | 42162 | 42162 |  | u8 | 1 | 0 | 0 | 0 | R
42163 | External ERS 3 accessory EB17 | Indicates if the status of ERS accessory EB17. I = closed, 0 = open. |  |  |  |  | 42163 | 42163 | 42163 | 42163 |  | 42163 | 42163 | 42163 |  | u8 | 1 | 0 | 0 | 0 | R
42164 | External ERS 2 accessory EB17 | Indicates if the status of ERS accessory EB17. I = closed, 0 = open. |  |  |  |  | 42164 | 42164 | 42164 | 42164 |  | 42164 | 42164 | 42164 |  | u8 | 1 | 0 | 0 | 0 | R
42166 | EB108-EP15 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42166 | 42166 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42168 | EB108-EP15 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42168 | 42168 | 42168 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42170 | EB108-EP15 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42170 | 42170 | 42170 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42172 | EB108-EP15 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42172 | 42172 | 42172 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42174 | EB108-EP15 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42174 | 42174 | 42174 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42176 | EB108-EP15 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42176 | 42176 | 42176 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42178 | EB108-EP15 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42178 | 42178 | 42178 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42181 | EB108-EP14 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42181 | 42181 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42183 | EB108-EP14 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42183 | 42183 | 42183 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42185 | EB108-EP14 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42185 | 42185 | 42185 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42187 | EB108-EP14 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42187 | 42187 | 42187 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42189 | EB108-EP14 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42189 | 42189 | 42189 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42191 | EB108-EP14 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42191 | 42191 | 42191 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42193 | EB108-EP14 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42193 | 42193 | 42193 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42196 | EB107-EP15 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42196 | 42196 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42198 | EB107-EP15 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42198 | 42198 | 42198 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42200 | EB107-EP15 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42200 | 42200 | 42200 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42202 | EB107-EP15 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42202 | 42202 | 42202 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42204 | EB107-EP15 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42204 | 42204 | 42204 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42206 | EB107-EP15 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42206 | 42206 | 42206 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42208 | EB107-EP15 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42208 | 42208 | 42208 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42211 | EB107-EP14 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42211 | 42211 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42213 | EB107-EP14 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42213 | 42213 | 42213 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42215 | EB107-EP14 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42215 | 42215 | 42215 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42217 | EB107-EP14 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42217 | 42217 | 42217 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42219 | EB107-EP14 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42219 | 42219 | 42219 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42221 | EB107-EP14 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42221 | 42221 | 42221 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42223 | EB107-EP14 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42223 | 42223 | 42223 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42226 | EB106-EP15 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42226 | 42226 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42228 | EB106-EP15 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42228 | 42228 | 42228 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42230 | EB106-EP15 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42230 | 42230 | 42230 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42232 | EB106-EP15 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42232 | 42232 | 42232 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42234 | EB106-EP15 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42234 | 42234 | 42234 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42236 | EB106-EP15 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42236 | 42236 | 42236 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42238 | EB106-EP15 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42238 | 42238 | 42238 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42241 | EB106-EP14 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42241 | 42241 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42243 | EB106-EP14 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42243 | 42243 | 42243 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42245 | EB106-EP14 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42245 | 42245 | 42245 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42247 | EB106-EP14 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42247 | 42247 | 42247 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42249 | EB106-EP14 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42249 | 42249 | 42249 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42251 | EB106-EP14 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42251 | 42251 | 42251 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42253 | EB106-EP14 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42253 | 42253 | 42253 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42256 | EB105-EP15 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42256 | 42256 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42258 | EB105-EP15 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42258 | 42258 | 42258 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42260 | EB105-EP15 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42260 | 42260 | 42260 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42262 | EB105-EP15 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42262 | 42262 | 42262 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42264 | EB105-EP15 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42264 | 42264 | 42264 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42266 | EB105-EP15 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42266 | 42266 | 42266 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42268 | EB105-EP15 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42268 | 42268 | 42268 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42271 | EB105-EP14 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42271 | 42271 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42273 | EB105-EP14 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42273 | 42273 | 42273 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42275 | EB105-EP14 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42275 | 42275 | 42275 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42277 | EB105-EP14 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42277 | 42277 | 42277 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42279 | EB105-EP14 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42279 | 42279 | 42279 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42281 | EB105-EP14 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42281 | 42281 | 42281 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42283 | EB105-EP14 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42283 | 42283 | 42283 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42286 | EB104-EP15 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42286 | 42286 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42288 | EB104-EP15 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42288 | 42288 | 42288 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42290 | EB104-EP15 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42290 | 42290 | 42290 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42292 | EB104-EP15 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42292 | 42292 | 42292 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42294 | EB104-EP15 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42294 | 42294 | 42294 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42296 | EB104-EP15 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42296 | 42296 | 42296 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42298 | EB104-EP15 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42298 | 42298 | 42298 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42301 | EB104-EP14 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42301 | 42301 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42303 | EB104-EP14 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42303 | 42303 | 42303 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42305 | EB104-EP14 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42305 | 42305 | 42305 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42307 | EB104-EP14 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42307 | 42307 | 42307 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42309 | EB104-EP14 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42309 | 42309 | 42309 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42311 | EB104-EP14 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42311 | 42311 | 42311 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42313 | EB104-EP14 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42313 | 42313 | 42313 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42316 | EB103-EP15 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42316 | 42316 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42318 | EB103-EP15 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42318 | 42318 | 42318 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42320 | EB103-EP15 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42320 | 42320 | 42320 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42322 | EB103-EP15 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42322 | 42322 | 42322 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42324 | EB103-EP15 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42324 | 42324 | 42324 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42326 | EB103-EP15 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42326 | 42326 | 42326 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42328 | EB103-EP15 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42328 | 42328 | 42328 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42331 | EB103-EP14 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42331 | 42331 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42333 | EB103-EP14 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42333 | 42333 | 42333 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42335 | EB103-EP14 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42335 | 42335 | 42335 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42337 | EB103-EP14 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42337 | 42337 | 42337 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42339 | EB103-EP14 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42339 | 42339 | 42339 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42341 | EB103-EP14 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42341 | 42341 | 42341 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42343 | EB103-EP14 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42343 | 42343 | 42343 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42346 | EB102-EP15 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42346 | 42346 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42348 | EB102-EP15 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42348 | 42348 | 42348 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42350 | EB102-EP15 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42350 | 42350 | 42350 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42352 | EB102-EP15 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42352 | 42352 | 42352 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42354 | EB102-EP15 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42354 | 42354 | 42354 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42356 | EB102-EP15 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42356 | 42356 | 42356 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42358 | EB102-EP15 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42358 | 42358 | 42358 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42361 | EB102-EP14 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42361 | 42361 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42363 | EB102-EP14 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42363 | 42363 | 42363 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42365 | EB102-EP14 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42365 | 42365 | 42365 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42367 | EB102-EP14 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42367 | 42367 | 42367 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42369 | EB102-EP14 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42369 | 42369 | 42369 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42371 | EB102-EP14 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42371 | 42371 | 42371 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42373 | EB102-EP14 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42373 | 42373 | 42373 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42376 | EB101-EP15 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42376 | 42376 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42378 | EB101-EP15 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42378 | 42378 | 42378 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42380 | EB101-EP15 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42380 | 42380 | 42380 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42382 | EB101-EP15 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42382 | 42382 | 42382 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42384 | EB101-EP15 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42384 | 42384 | 42384 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42386 | EB101-EP15 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42386 | 42386 | 42386 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42388 | EB101-EP15 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42388 | 42388 | 42388 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42391 | EB101-EP14 Heat Meter - Pool2 Cpr | Accumulated energy production as calculated by the heat meter | [6 empty] | 42391 | 42391 |  |  |  |  | kWh | u32 | 10 | 0 | 0 | 0 | R
42393 | EB101-EP14 Heat Meter - HW Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42393 | 42393 | 42393 |  |  | 42393 | 42393 | kWh | u32 | 10 | 0 | 0 | 0 | R
42395 | EB101-EP14 Heat Meter - Heat Cpr and Add | Accumulated energy production as calculated by the heat meter | [5 empty] | 42395 | 42395 | 42395 |  |  | 42395 | 42395 | kWh | u32 | 10 | 0 | 0 | 0 | R
42397 | EB101-EP14 Heat Meter - Cooling Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42397 | 42397 | 42397 |  |  | 42397 | 42397 | kWh | u32 | 10 | 0 | 0 | 0 | R
42399 | EB101-EP14 Heat Meter - Pool Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42399 | 42399 | 42399 |  |  | 42399 | 42399 | kWh | u32 | 10 | 0 | 0 | 0 | R
42401 | EB101-EP14 Heat Meter - HW Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42401 | 42401 | 42401 |  |  | 42401 | 42401 | kWh | u32 | 10 | 0 | 0 | 0 | R
42403 | EB101-EP14 Heat Meter - Heat Cpr | Accumulated energy production as calculated by the heat meter | [5 empty] | 42403 | 42403 | 42403 |  |  | 42403 | 42403 | kWh | u32 | 10 | 0 | 0 | 0 | R
42435 | Heat Meter - HW Cpr and Add - Total system | Accumulated energy production as calculated by the heat meter, summaries of all heat pumps in system | [6 empty] | 42435 | 42435 |  |  | 42435 | 42435 | kWh | u32 | 10 | 0 | 0 | 0 | R
42437 | Heat Meter - HW Cpr and Add - Total system | Accumulated energy production as calculated by the heat meter, summaries of all heat pumps in system |  |  | 42437 | 42437 | 42437 | 42437 |  |  |  |  | 42437 | 42437 | kWh | u32 | 10 | 0 | 0 | 0 | R
42439 | Heat Meter - Heat Cpr and Add - Total system | Accumulated energy production as calculated by the heat meter, summaries of all heat pumps in system |  |  | 42439 | 42439 | 42439 | 42439 | 42439 | 42439 |  |  | 42439 | 42439 | kWh | u32 | 10 | 0 | 0 | 0 | R
42441 | Heat Meter - Cooling Cpr - Total system | Accumulated energy production as calculated by the heat meter, summaries of all heat pumps in system |  |  |  |  | 42441 | 42441 | 42441 | 42441 |  |  | 42441 | 42441 | kWh | u32 | 10 | 0 | 0 | 0 | R
42443 | Heat Meter - Pool Cpr - Total system | Accumulated energy production as calculated by the heat meter, summaries of all heat pumps in system |  |  | 42443 | 42443 | 42443 | 42443 | 42443 | 42443 |  |  | 42443 | 42443 | kWh | u32 | 10 | 0 | 0 | 0 | R
42445 | Heat Meter - HW Cpr - Total system | Accumulated energy production as calculated by the heat meter, summaries of all heat pumps in system |  |  | 42445 | 42445 | 42445 | 42445 | 42445 | 42445 |  |  | 42445 | 42445 | kWh | u32 | 10 | 0 | 0 | 0 | R
42447 | Heat Meter - Heat Cpr - Total system | Accumulated energy production as calculated by the heat meter, summaries of all heat pumps in system |  |  | 42447 | 42447 | 42447 | 42447 | 42447 | 42447 |  |  | 42447 | 42447 | kWh | u32 | 10 | 0 | 0 | 0 | R
42464 | External ERS 4 fire place guard | [5 empty] | 42464 | 42464 | 42464 | 42464 |  | 42464 | 42464 | 42464 |  | u8 | 1 | 0 | 0 | 0 | R
42465 | External ERS 3 fire place guard | [5 empty] | 42465 | 42465 | 42465 | 42465 |  | 42465 | 42465 | 42465 |  | u8 | 1 | 0 | 0 | 0 | R
42466 | External ERS 2 fire place guard | [5 empty] | 42466 | 42466 | 42466 | 42466 |  | 42466 | 42466 | 42466 |  | u8 | 1 | 0 | 0 | 0 | R
42467 | External ERS 1 fire place guard | [5 empty] | 42467 | 42467 | 42467 | 42467 |  | 42467 | 42467 | 42467 |  | u8 | 1 | 0 | 0 | 0 | R
42468 | EB108 External Energy Meter 2 Accumulated Energy | [6 empty] | 42468 | 42468 | 42468 |  | 42468 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42470 | EB108 External Energy Meter 1 Accumulated Energy | [6 empty] | 42470 | 42470 | 42470 |  | 42470 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42472 | EB107 External Energy Meter 2 Accumulated Energy | [6 empty] | 42472 | 42472 | 42472 |  | 42472 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42474 | EB107 External Energy Meter 1 Accumulated Energy | [6 empty] | 42474 | 42474 | 42474 |  | 42474 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42476 | EB106 External Energy Meter 2 Accumulated Energy | [6 empty] | 42476 | 42476 | 42476 |  | 42476 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42478 | EB106 External Energy Meter 1 Accumulated Energy | [6 empty] | 42478 | 42478 | 42478 |  | 42478 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42480 | EB105 External Energy Meter 2 Accumulated Energy | [6 empty] | 42480 | 42480 | 42480 |  | 42480 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42482 | EB105 External Energy Meter 1 Accumulated Energy | [6 empty] | 42482 | 42482 | 42482 |  | 42482 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42484 | EB104 External Energy Meter 2 Accumulated Energy | [6 empty] | 42484 | 42484 | 42484 |  | 42484 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42486 | EB104 External Energy Meter 1 Accumulated Energy | [6 empty] | 42486 | 42486 | 42486 |  | 42486 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42488 | EB103 External Energy Meter 2 Accumulated Energy | [6 empty] | 42488 | 42488 | 42488 |  | 42488 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42490 | EB103 External Energy Meter 1 Accumulated Energy | [6 empty] | 42490 | 42490 | 42490 |  | 42490 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42492 | EB102 External Energy Meter 2 Accumulated Energy | [6 empty] | 42492 | 42492 | 42492 |  | 42492 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42494 | EB102 External Energy Meter 1 Accumulated Energy | [6 empty] | 42494 | 42494 | 42494 |  | 42494 |  |  | kWh | u32 | 1 | 0 | 0 | 0 | R
42496 | EB101 External Energy Meter 2 Accumulated Energy | [6 empty] | 42496 | 42496 | 42496 |  | 42496 | 42496 | 42496 | kWh | u32 | 1 | 0 | 0 | 0 | R
42498 | EB101 External Energy Meter 1 Accumulated Energy | [6 empty] | 42498 | 42498 | 42498 |  | 42498 | 42498 | 42498 | kWh | u32 | 1 | 0 | 0 | 0 | R
42504 | External Energy Meter Accumulated System |  |  |  | 42504 | 42504 | 42504 | 42504 | 42504 | 42504 |  | 42504 | 42504 | 42504 | kWh | u32 | 1 | 0 | 0 | 0 | R
43001 | Software version |  | 43001 | 43001 | 43001 | 43001 | 43001 | 43001 | 43001 | 43001 | 43001 | 43001 | 43001 | 43001 |  | u16 | 1 | 0 | 0 | 0 | R
43005 | Degree Minutes (16 bit) | Degree minutes, 16bit value (-32768 < x < 32767). Values outside valid values are rounded to the closest valid value. |  |  | 43005 | 43005 | 43005 | 43005 | 43005 | 43005 | 43005 | 43005 | 43005 | 43005 |  | s16 | 10 | -30000 | 30000 | 0 | R/W
43006 | Calc. Supply S4 | Calculated supply temperature for the climate system | 43006 | 43006 | 43006 | 43006 | 43006 | 43006 | 43006 | 43006 |  | 43006 | 43006 | 43006 | °C | s16 | 10 | 0 | 0 | 0 | R
43007 | Calc. Supply S3 | Calculated supply temperature for the climate system | 43007 | 43007 | 43007 | 43007 | 43007 | 43007 | 43007 | 43007 |  | 43007 | 43007 | 43007 | °C | s16 | 10 | 0 | 0 | 0 | R
43008 | Calc. Supply S2 | Calculated supply temperature for the climate system | 43008 | 43008 | 43008 | 43008 | 43008 | 43008 | 43008 | 43008 |  | 43008 | 43008 | 43008 | °C | s16 | 10 | 0 | 0 | 0 | R
43009 | Calc. Supply S1 | Calculated supply temperature for the climate system | 43009 | 43009 | 43009 | 43009 | 43009 | 43009 | 43009 | 43009 | 43009 | 43009 | 43009 | 43009 | °C | s16 | 10 | 0 | 0 | 0 | R
43013 | Freeze Protection Status | 1 = Freeze protection active | 43013 | 43013 | 43013 | 43013 | 43013 | 43013 | 43013 | 43013 | 43013 | 43013 | 43013 | 43013 |  | u8 | 1 | 0 | 0 | 0 | R
43024 | Status Cooling | 0=Off 1=On |  |  |  |  | 43024 | 43024 |  |  | 43024 | 43024 | 43024 | 43024 |  | u8 | 1 | 0 | 0 | 0 | R
43061 | t. after start timer |  |  |  | 43061 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
43062 | t. after mode change | Time after mode change |  |  | 43062 | 43062 | [9 empty] | u8 | 1 | 0 | 0 | 0 | R
43064 | Heat Medium Flow dT Set Point | Set point delta T for the heat medium flow |  |  | 43064 | 43064 | 43064 | 43064 | 43064 | 43064 | [5 empty] | s16 | 10 | 0 | 0 | 0 | R
43065 | Heat Medium Flow dT Actual | Current value of the delta T for the heat medium flow |  |  | 43065 | 43065 | 43065 | 43065 | 43065 | 43065 | 43065 | 43065 |  | 43065 |  | s16 | 10 | 0 | 0 | 0 | R
43066 | Defrosting time | Defrosting time |  |  | 43066 | 43066 | [8 empty] | s | s16 | 1 | 0 | 0 | 0 | R
43081 | Tot. op.time add. | Total electric additive operation time | 43081 | 43081 | 43081 | 43081 | 43081 | 43081 | 43081 | 43081 | 43081 | 43081 | 43081 | 43081 | h | s32 | 10 | 0 | 1000000 | 0 | R
43084 | Int. el.add. Power | Current power from the internal electrical addition | 43084 | 43084 | 43084 | 43084 | 43084 | 43084 | 43084 | 43084 | 43084 | 43084 | 43084 | 43084 | kW | s16 | 100 | 0 | 0 | 0 | R
43086 | Prio | Indicates what heating action (HW/heat/pool) currently prioritised 10=Off 20=Hot Water 30=Heat 40=Pool 41=Pool 2 50=Transfer 60=Cooling | 43086 | 43086 | 43086 | 43086 | 43086 | 43086 | 43086 | 43086 | 43086 | 43086 | 43086 | 43086 |  | u8 | 1 | 0 | 0 | 0 | R
43091 | Int. el.add. State | Number of steps active for internal step-controlled addition | 43091 | 43091 | 43091 | 43091 | 43091 | 43091 | 43091 | 43091 | 43091 | 43091 | 43091 | 43091 |  | u8 | 1 | 0 | 0 | 0 | R
43093 | Mixing Valve State S4 | State of the mixing valve for the climate system | 43093 | 43093 | 43093 | 43093 | 43093 | 43093 | 43093 | 43093 |  | 43093 | 43093 | 43093 |  | u8 | 1 | 0 | 0 | 0 | R
43094 | Mixing Valve State S3 | State of the mixing valve for the climate system | 43094 | 43094 | 43094 | 43094 | 43094 | 43094 | 43094 | 43094 |  | 43094 | 43094 | 43094 |  | u8 | 1 | 0 | 0 | 0 | R
43095 | Mixing Valve State S2 | State of the mixing valve for the climate system | 43095 | 43095 | 43095 | 43095 | 43095 | 43095 | 43095 | 43095 |  | 43095 | 43095 | 43095 |  | u8 | 1 | 0 | 0 | 0 | R
43096 | Mixing Valve State S1 | State of the mixing valve for the climate system | 43096 | 43096 | 43096 | 43096 | 43096 | 43096 | 43096 | 43096 | 43096 | 43096 | 43096 | 43096 |  | u8 | 1 | 0 | 0 | 0 | R
43097 | Status of the shunt controlled additional heat accessory | 10 = Off, 20 = Running, 30 = Passive |  |  | 43097 |  | 43097 | 43097 | 43097 | 43097 |  | 43097 | 43097 |  |  | u8 | 1 | 0 | 0 | 0 | R
43103 | HPAC state | State of the HPAC cooling accessory. |  |  |  |  | 43103 | 43103 | 43103 | 43103 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43105 | Status FJVM | The state of the FJVM accessory | 43105 | 43105 | [11 empty] | u8 | 1 | 0 | 0 | 0 | R
43108 | Fan speed current | The current fan speed after scheduling and blocks are considered | 43108 | 43108 | 43108 | 43108 | 43108 | 43108 | 43108 | 43108 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43122 | Compr. current min.freq. | The current minimum frequency of the compressor |  |  | 43122 | 43122 | 43122 |  | 43122 | [5 empty] | Hz | s16 | 1 | 0 | 0 | 0 | R
43123 | Compr. current max.freq. | The current maximum frequency of the compressor |  |  | 43123 | 43123 | 43123 | [7 empty] | Hz | s16 | 1 | 0 | 0 | 0 | R
43124 | Airflow ref. | Reference value for the airflow. |  |  | 43124 | 43124 | [9 empty] | s16 | 10 | 0 | 0 | 0 | R
43132 | Inverter com. timer | This value shows the time since last communication with the inverter |  |  | 43132 | 43132 | 43132 |  | 43132 | [5 empty] | sec | u16 | 1 | 0 | 0 | 0 | R
43136 | Compressor Frequency, Actual | The compressor frequency the compressor is currently running at |  |  | 43136 | 43136 | 43136 |  | 43136 | [5 empty] | Hz | u16 | 10 | 0 | 0 | 0 | R
43140 | Inverter Temperature | Current inverter temparture |  |  | 43140 | 43140 | 43140 |  | 43140 | [5 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
43141 | compr. in power | The power delivered from the inverter to the compressor |  |  | 43141 | 43141 | 43141 |  | 43141 | [5 empty] | W | u16 | 1 | 0 | 0 | 0 | R
43144 | Compr. energy total | Total compressor energy in kWh |  |  | 43144 | [9 empty] | kWh | u32 | 100 | 0 | 9999999 | 0 | R
43147 | Compr. in current | The current delivered from the inverter to the compressor |  |  | 43147 | 43147 | 43147 |  | 43147 | [5 empty] | A | s16 | 1 | 0 | 0 | 0 | R
43152 | Internal cooling blocked | [5 empty] | 43152 | 43152 | [7 empty] | u8 | 1 | 0 | 0 | 0 | R
43158 | External adjustment activated via input S4 |  | 43158 | 43158 | 43158 | 43158 | 43158 | 43158 | 43158 | 43158 |  | 43158 | 43158 | 43158 |  | u8 | 1 | 0 | 0 | 0 | R
43159 | External adjustment activated via input S3 |  | 43159 | 43159 | 43159 | 43159 | 43159 | 43159 | 43159 | 43159 |  | 43159 | 43159 | 43159 |  | u8 | 1 | 0 | 0 | 0 | R
43160 | External adjustment activated via input S2 |  | 43160 | 43160 | 43160 | 43160 | 43160 | 43160 | 43160 | 43160 |  | 43160 | 43160 | 43160 |  | u8 | 1 | 0 | 0 | 0 | R
43161 | External adjustment activated via input S1 |  | 43161 | 43161 | 43161 | 43161 | 43161 | 43161 | 43161 | 43161 | 43161 | 43161 | 43161 | 43161 |  | u8 | 1 | 0 | 0 | 0 | R
43163 | Blocking status of the shunt controlled add heat acc | 0 = Unblocked, 1 = Blocked |  |  |  |  | 43163 | 43163 | 43163 | 43163 |  | 43163 | 43163 |  |  | u8 | 1 | 0 | 0 | 0 | R
43164 | Cooling blocked | Whether cooling is blocked |  |  |  |  | 43164 | 43164 | 43164 | 43164 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43171 | Blocking status of the step controlled add heat acc | 0 = Unblocked, 1 = Blocked |  |  |  |  | 43171 | 43171 | 43171 | 43171 | 43171 | 43171 | 43171 | 43171 |  | u8 | 1 | 0 | 0 | 0 | R
43180 | HWC Pump Status GP11 | Hot water circulation pump status. 1=on, 0=off | 43180 | 43180 | 43180 |  | 43180 | 43180 | 43180 | 43180 |  |  |  | 43180 |  | u8 | 1 | 0 | 0 | 0 | R
43181 | Chargepump speed |  |  |  | 43181 | [9 empty] | % | u8 | 1 | 0 | 0 | 0 | R
43182 | Compressor Frequency, Target | The targeted compressor frequency, before excluding any blocked frequencies |  |  | 43182 | 43182 | 43182 | [7 empty] | Hz | u16 | 1 | 0 | 0 | 0 | R
43189 | GP10 Ext. Supply Pump Status | External supply pump status. 1=on,0=off |  |  |  | 43189 |  | 43189 | 43189 | 43189 | 43189 | 43189 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43230 | Heat Meter (OBSOLETE) | Obsolete since v4798 of the controller software | [5 empty] | 43230 |  |  |  | 43230 | 43230 | 43230 | kWh | u32 | 10 | 0 | 9999999 | 0 | R
43239 | Tot. HW op.time add. | Total electric additive operation time in hot water mode | 43239 | 43239 | 43239 | 43239 | 43239 | 43239 | 43239 | 43239 | 43239 | 43239 | 43239 | 43239 | h | s32 | 10 | 0 | 9999999 | 0 | R
43305 | Compr. energy HW | Compressor energy during hot water production in kWh |  |  | 43305 | [9 empty] | kWh | u32 | 100 | 0 | 9999999 | 0 | R
43371 | Hot gas limit status |  |  |  | 43371 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
43372 | Evaporater limit status |  |  |  | 43372 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
43375 | compr. in power mean | Mean power delivered from the inverter to the compressor. Mean is calculated every 10 seconds. |  |  | 43375 | 43375 | 43375 |  | 43375 | [5 empty] | W | s16 | 1 | 0 | 0 | 0 | R
43382 | Inverter mem error code |  |  |  | 43382 | [10 empty] | u16 | 1 | 0 | 0 | 0 | R
43383 | FJVM Relays | Indicates the active relays on the FJVM accessory. The information is binary encoded | 43383 | 43383 | [11 empty] | u8 | 1 | 0 | 0 | 0 | R
43395 | HPAC Relays | Indicates the active relays on the HPAC accessory. The information is binary encoded |  |  |  |  | 43395 | 43395 | [7 empty] | u8 | 1 | 0 | 0 | 0 | R
43414 | Compressor starts EB100-EP15 | Number of compressorer starts | [6 empty] | 43414 | 43414 | [5 empty] | s32 | 1 | 0 | 0 | 0 | R
43416 | Compressor starts EB100-EP14 | Number of compressorer starts | 43416 | 43416 | 43416 | 43416 | 43416 | 43416 | 43416 | 43416 | [5 empty] | s32 | 1 | 0 | 9999999 | 0 | R
43418 | Tot. op.time compr. EB100-EP15 | Total compressorer operation time | [6 empty] | 43418 | 43418 |  |  |  |  | h | s32 | 1 | 0 | 0 | 0 | R
43420 | Tot. op.time compr. EB100-EP14 | Total compressorer operation time | 43420 | 43420 | 43420 | 43420 | 43420 | 43420 | 43420 | 43420 |  |  |  |  | h | s32 | 1 | 0 | 9999999 | 0 | R
43422 | Tot. HW op.time compr. EB100-EP15 | Total compressorer operation time in hot water mode | [6 empty] | 43422 | 43422 |  |  |  |  | h | s32 | 1 | 0 | 0 | 0 | R
43424 | Tot. HW op.time compr. EB100-EP14 | Total compressorer operation time in hot water mode | 43424 | 43424 | 43424 | 43424 | 43424 | 43424 | 43424 | 43424 |  |  |  |  | h | s32 | 1 | 0 | 9999999 | 0 | R
43426 | Compressor State EP15 | 20 = Stopped, 40 = Starting, 60 = Running, 100 = Stopping | [6 empty] | 43426 | 43426 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43427 | Compressor State EP14 | 20 = Stopped, 40 = Starting, 60 = Running, 100 = Stopping | 43427 | 43427 | 43427 | 43427 | 43427 | 43427 | 43427 | 43427 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43430 | Supply Pump State EP15 | 10=off,15=starting,20=on,40=10-day mode,80=calibration | [6 empty] | 43430 | 43430 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43431 | Supply Pump State EP14 | 10=off,15=starting,20=on,40=10-day mode,80=calibration | 43431 | 43431 | 43431 | 43431 | 43431 | 43431 | 43431 | 43431 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43432 | Brine Pump State EP15 | 10=off,15=starting,20=on,40=10-day mode,80=calibration | [6 empty] | 43432 | 43432 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43433 | Brine Pump State EP14 | 10=off,15=starting,20=on,40=10-day mode,80=calibration |  |  |  |  | 43433 | 43433 | 43433 | 43433 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43434 | Cpr Status EP15 | Status of the compressor. 1=on,0=off 0=Off 1=On | [6 empty] | 43434 | 43434 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43435 | Cpr Status EP14 | Status of the compressor. 1=on,0=off 0=Off 1=On | 43435 | 43435 | 43435 | 43435 | 43435 | 43435 | 43435 | 43435 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43436 | Supply Pump Speed EP15 | Supply pump speed in % | [6 empty] | 43436 | 43436 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43437 | Supply Pump Speed EP14 | Supply pump speed in % |  |  | 43437 | 43437 | 43437 | 43437 | 43437 | 43437 |  |  | 43437 | 43437 | % | u8 | 1 | 0 | 0 | 0 | R
43438 | EP15-GP2 Brine Pump Status | Brine pump speed in % | [6 empty] | 43438 | 43438 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43439 | EP14-GP2 Brine Pump Status EP14 | Brine pump speed in % |  |  |  |  | 43439 | 43439 | 43439 | 43439 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43444 | State OEK | The state of the OEK accessory |  |  | 43444 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
43460 | State DEH | The state of the DEH accessory | 43460 | 43460 | [11 empty] | u8 | 1 | 0 | 0 | 0 | R
43473 | Docked Heat Compressors | Number of compressors docked to heating | [5 empty] | 43473 | 43473 | 43473 | 43473 | 43473 | 43473 | 43473 |  | u8 | 1 | 0 | 0 | 0 | R
43474 | Docked Hot Water Compressors | Number of compressors docked to hot water | [5 empty] | 43474 | 43474 | 43474 | 43474 | 43474 | 43474 | 43474 |  | u8 | 1 | 0 | 0 | 0 | R
43475 | Docked Pool 1 Compressors | Number of compressors docked to pool 1 | [5 empty] | 43475 | 43475 | 43475 |  | 43475 | 43475 | 43475 |  | u8 | 1 | 0 | 0 | 0 | R
43481 | QN10 State | 0=Heating, 1=Hot water | [6 empty] | 43481 | 43481 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43484 | FLM 4 Cooling Status | Whether FLM cooling is active, 1=yes, 0=no |  |  |  |  | 43484 | 43484 | 43484 | 43484 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43485 | FLM 3 Cooling Status | Whether FLM cooling is active, 1=yes, 0=no |  |  |  |  | 43485 | 43485 | 43485 | 43485 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43486 | FLM 2 Cooling Status | Whether FLM cooling is active, 1=yes, 0=no |  |  |  |  | 43486 | 43486 | 43486 | 43486 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43487 | FLM 1 Cooling Status | Whether FLM cooling is active, 1=yes, 0=no |  |  |  |  | 43487 | 43487 | 43487 | 43487 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43490 | Steps ext. add. | Number of steps active external addition | [6 empty] | 43490 | 43490 |  |  | 43490 | 43490 |  | u8 | 1 | 0 | 0 | 0 | R
43513 | EB100-EP15 PCA Base Relays | Indicates active relays on the PCA Base card. Please refer to the wiring diagram for relay description. Binary encoded. 1=on, 0=off. Bit0=K4,Bit1=K3,Bit2=K2,Bit3=K1 | [6 empty] | 43513 | 43513 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43514 | EB100-EP14 PCA Base Relays | Indicates active relays on the PCA Base card. Please refer to the wiring diagram for relay description. Binary encoded. 1=on, 0=off. Bit0=K4,Bit1=K3,Bit2=K2,Bit3=K1 | 43514 | 43514 | 43514 | 43514 | 43514 | 43514 | 43514 | 43514 | 43514 | 43514 | 43514 | 43514 |  | u8 | 1 | 0 | 0 | 0 | R
43516 | PCA-Power Relays EP14 | Indicates the active relays on the PCA-Power card. The information is binary encoded | 43516 | 43516 | 43516 | 43516 | 43516 | 43516 | 43516 | 43516 | 43516 | 43516 | 43516 | 43516 |  | u8 | 1 | 0 | 0 | 0 | R
43536 | Ext. Addition Blocked | [12 empty] | 43536 |  | u8 | 1 | 0 | 0 | 0 | R
43542 | Calculated supply air temp. |  |  |  | 43542 |  | 43542 | [7 empty] | °C | s16 | 10 | 0 | 0 | 0 | R
43555 | HW Comfort Shunt State | 10=shunt off,20=shunt open,30=shunt closed |  |  |  |  | 43555 | 43555 | 43555 | 43555 |  | 43555 | 43555 |  |  | u8 | 1 | 0 | 0 | 0 | R
43556 | HW Comfort Add Status | 1=on,0=off |  |  |  |  | 43556 | 43556 | 43556 | 43556 |  | 43556 | 43556 |  |  | u8 | 1 | 0 | 0 | 0 | R
43560 | Pool 2 blocked | [5 empty] | 43560 | 43560 | 43560 | 43560 |  | 43560 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43561 | Pool 1 blocked |  |  |  | 43561 |  | 43561 | 43561 | 43561 | 43561 |  | 43561 | 43561 | 43561 |  | u8 | 1 | 0 | 0 | 0 | R
43563 | GP9 Pool 2 Valve | [5 empty] | 43563 | 43563 | 43563 | 43563 |  | 43563 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43564 | GP9 Pool 1 Valve | [5 empty] | 43564 | 43564 | 43564 | 43564 |  | 43564 | 43564 | 43564 |  | u8 | 1 | 0 | 0 | 0 | R
43577 | Docked Pool 2 Compressors | Number of compressors docked to pool 2 | [5 empty] | 43577 | 43577 | 43577 |  | 43577 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43580 | EB108 Version | [6 empty] | 43580 | 43580 | 43580 |  | 43580 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43598 | EB108 Slave Type | [6 empty] | 43598 | 43598 | 43598 |  | 43598 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43599 | EB108 Compressor EP14 Size | [6 empty] | 43599 | 43599 | 43599 |  | 43599 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
43600 | EB108-EP15-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43600 | 43600 | 43600 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43601 | EB108-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43601 | 43601 | 43601 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43602 | EB108-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43602 | 43602 | 43602 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43603 | EB108-EP15-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43603 | 43603 | 43603 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43604 | EB108-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43604 | 43604 | 43604 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43605 | EB108-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43605 | 43605 | 43605 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43606 | EB108-EP15-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43606 | 43606 | 43606 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43607 | EB108-EP15-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43607 | 43607 | 43607 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43608 | EB108-EP15-BP8 Pressure Transmitter | [6 empty] | 43608 | 43608 | 43608 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43609 | EB108-EP15 Compressor State | On/Off | [5 empty] | 43609 | 43609 | 43609 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43610 | EB108-EP15 Compr. time to start | [6 empty] | 43610 | 43610 | 43610 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43611 | EB108-EP15 Relay status | [6 empty] | 43611 | 43611 | 43611 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43612 | EB108-EP15 Heat med. pump status | [6 empty] | 43612 | 43612 | 43612 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43613 | EB108-EP15 Brine pump status | [6 empty] | 43613 | 43613 | 43613 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43614 | EB108-EP15 Compressor starts | [6 empty] | 43614 | 43614 | 43614 | [5 empty] | u32 | 1 | 0 | 0 | 0 | R
43616 | EB108-EP15 Tot. op.time compr | [6 empty] | 43616 | 43616 | 43616 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43618 | EB108-EP15 Tot. HW op.time compr | [6 empty] | 43618 | 43618 | 43618 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43620 | EB108-EP15 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43620 | 43620 | 43620 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43621 | EB108-EP14-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43621 | 43621 | 43621 |  | 43621 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43622 | EB108-EP14-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43622 | 43622 | 43622 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43623 | EB108-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43623 | 43623 | 43623 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43624 | EB108-EP14-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43624 | 43624 | 43624 |  | 43624 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43625 | EB108-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43625 | 43625 | 43625 |  | 43625 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43626 | EB108-EP14-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43626 | 43626 | 43626 |  | 43626 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43627 | EB108-EP14-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43627 | 43627 | 43627 |  | 43627 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43628 | EB108-EP14-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43628 | 43628 | 43628 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43629 | EB108-EP14-BP8 Pressure Transmitter | [6 empty] | 43629 | 43629 | 43629 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43630 | EB108-EP14 Compressor State | On/Off | [5 empty] | 43630 | 43630 | 43630 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43631 | EB108-EP14 Compr. time to start | [6 empty] | 43631 | 43631 | 43631 |  | 43631 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43632 | EB108-EP14 Relay status | [6 empty] | 43632 | 43632 | 43632 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43633 | EB108-EP14 Heat med. pump status | [6 empty] | 43633 | 43633 | 43633 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43634 | EB108-EP14 Brine pump status | [6 empty] | 43634 | 43634 | 43634 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43635 | EB108-EP14 Compressor starts | [6 empty] | 43635 | 43635 | 43635 |  | 43635 |  |  |  | u32 | 1 | 0 | 9999999 | 0 | R
43637 | EB108-EP14 Tot. op.time compr | [6 empty] | 43637 | 43637 | 43637 |  | 43637 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43639 | EB108-EP14 Tot. HW op.time compr | [6 empty] | 43639 | 43639 | 43639 |  | 43639 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43641 | EB108-EP14 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43641 | 43641 | 43641 |  | 43641 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43642 | EB107 Version | [6 empty] | 43642 | 43642 | 43642 |  | 43642 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43660 | EB107 Slave Type | [6 empty] | 43660 | 43660 | 43660 |  | 43660 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43661 | EB107 Compressor EP14 Size | [6 empty] | 43661 | 43661 | 43661 |  | 43661 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
43662 | EB107-EP15-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43662 | 43662 | 43662 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43663 | EB107-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43663 | 43663 | 43663 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43664 | EB107-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43664 | 43664 | 43664 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43665 | EB107-EP15-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43665 | 43665 | 43665 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43666 | EB107-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43666 | 43666 | 43666 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43667 | EB107-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43667 | 43667 | 43667 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43668 | EB107-EP15-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43668 | 43668 | 43668 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43669 | EB107-EP15-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43669 | 43669 | 43669 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43670 | EB107-EP15-BP8 Pressure Transmitter | [6 empty] | 43670 | 43670 | 43670 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43671 | EB107-EP15 Compressor State | On/Off | [5 empty] | 43671 | 43671 | 43671 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43672 | EB107-EP15 Compr. time to start | [6 empty] | 43672 | 43672 | 43672 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43673 | EB107-EP15 Relay status | [6 empty] | 43673 | 43673 | 43673 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43674 | EB107-EP15 Heat med. pump status | [6 empty] | 43674 | 43674 | 43674 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43675 | EB107-EP15 Brine pump status | [6 empty] | 43675 | 43675 | 43675 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43676 | EB107-EP15 Compressor starts | [6 empty] | 43676 | 43676 | 43676 | [5 empty] | u32 | 1 | 0 | 0 | 0 | R
43678 | EB107-EP15 Tot. op.time compr | [6 empty] | 43678 | 43678 | 43678 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43680 | EB107-EP15 Tot. HW op.time compr | [6 empty] | 43680 | 43680 | 43680 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43682 | EB107-EP15 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43682 | 43682 | 43682 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43683 | EB107-EP14-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43683 | 43683 | 43683 |  | 43683 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43684 | EB107-EP14-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43684 | 43684 | 43684 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43685 | EB107-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43685 | 43685 | 43685 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43686 | EB107-EP14-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43686 | 43686 | 43686 |  | 43686 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43687 | EB107-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43687 | 43687 | 43687 |  | 43687 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43688 | EB107-EP14-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43688 | 43688 | 43688 |  | 43688 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43689 | EB107-EP14-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43689 | 43689 | 43689 |  | 43689 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43690 | EB107-EP14-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43690 | 43690 | 43690 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43691 | EB107-EP14-BP8 Pressure Transmitter | [6 empty] | 43691 | 43691 | 43691 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43692 | EB107-EP14 Compressor State | [6 empty] | 43692 | 43692 | 43692 |  | 43692 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43693 | EB107-EP14 Compr. time to start | [6 empty] | 43693 | 43693 | 43693 |  | 43693 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43694 | EB107-EP14 Relay status | [6 empty] | 43694 | 43694 | 43694 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43695 | EB107-EP14 Heat med. pump status | [6 empty] | 43695 | 43695 | 43695 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43696 | EB107-EP14 Brine pump status | [6 empty] | 43696 | 43696 | 43696 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43697 | EB107-EP14 Compressor starts | [6 empty] | 43697 | 43697 | 43697 |  | 43697 |  |  |  | u32 | 1 | 0 | 9999999 | 0 | R
43699 | EB107-EP14 Tot. op.time compr | [6 empty] | 43699 | 43699 | 43699 |  | 43699 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43701 | EB107-EP14 Tot. HW op.time compr | [6 empty] | 43701 | 43701 | 43701 |  | 43701 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43703 | EB107-EP14 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43703 | 43703 | 43703 |  | 43703 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43704 | EB106 Version | [6 empty] | 43704 | 43704 | 43704 |  | 43704 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43722 | EB106 Slave Type | [6 empty] | 43722 | 43722 | 43722 |  | 43722 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43723 | EB106 Compressor EP14 Size | [6 empty] | 43723 | 43723 | 43723 |  | 43723 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
43724 | EB106-EP15-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43724 | 43724 | 43724 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43725 | EB106-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43725 | 43725 | 43725 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43726 | EB106-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43726 | 43726 | 43726 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43727 | EB106-EP15-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43727 | 43727 | 43727 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43728 | EB106-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43728 | 43728 | 43728 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43729 | EB106-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43729 | 43729 | 43729 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43730 | EB106-EP15-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43730 | 43730 | 43730 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43731 | EB106-EP15-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43731 | 43731 | 43731 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43732 | EB106-EP15-BP8 Pressure Transmitter | [6 empty] | 43732 | 43732 | 43732 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43733 | EB106-EP15 Compressor State | On/Off | [5 empty] | 43733 | 43733 | 43733 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43734 | EB106-EP15 Compr. time to start | [6 empty] | 43734 | 43734 | 43734 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43735 | EB106-EP15 Relay status | [6 empty] | 43735 | 43735 | 43735 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43736 | EB106-EP15 Heat med. pump status | [6 empty] | 43736 | 43736 | 43736 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43737 | EB106-EP15 Brine pump status | [6 empty] | 43737 | 43737 | 43737 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43738 | EB106-EP15 Compressor starts | [6 empty] | 43738 | 43738 | 43738 | [5 empty] | u32 | 1 | 0 | 0 | 0 | R
43740 | EB106-EP15 Tot. op.time compr | [6 empty] | 43740 | 43740 | 43740 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43742 | EB106-EP15 Tot. HW op.time compr | [6 empty] | 43742 | 43742 | 43742 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43744 | EB106-EP15 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43744 | 43744 | 43744 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43745 | EB106-EP14-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43745 | 43745 | 43745 |  | 43745 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43746 | EB106-EP14-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43746 | 43746 | 43746 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43747 | EB106-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43747 | 43747 | 43747 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43748 | EB106-EP14-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43748 | 43748 | 43748 |  | 43748 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43749 | EB106-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43749 | 43749 | 43749 |  | 43749 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43750 | EB106-EP14-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43750 | 43750 | 43750 |  | 43750 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43751 | EB106-EP14-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43751 | 43751 | 43751 |  | 43751 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43752 | EB106-EP14-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43752 | 43752 | 43752 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43753 | EB106-EP14-BP8 Pressure Transmitter | [6 empty] | 43753 | 43753 | 43753 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43754 | EB106-EP14 Compressor State | On/Off | [5 empty] | 43754 | 43754 | 43754 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43755 | EB106-EP14 Compr. time to start | [6 empty] | 43755 | 43755 | 43755 |  | 43755 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43756 | EB106-EP14 Relay status | [6 empty] | 43756 | 43756 | 43756 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43757 | EB106-EP14 Heat med. pump status | [6 empty] | 43757 | 43757 | 43757 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43758 | EB106-EP14 Brine pump status | [6 empty] | 43758 | 43758 | 43758 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43759 | EB106-EP14 Compressor starts | [6 empty] | 43759 | 43759 | 43759 |  | 43759 |  |  |  | u32 | 1 | 0 | 9999999 | 0 | R
43761 | EB106-EP14 Tot. op.time compr | [6 empty] | 43761 | 43761 | 43761 |  | 43761 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43763 | EB106-EP14 Tot. HW op.time compr | [6 empty] | 43763 | 43763 | 43763 |  | 43763 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43765 | EB106-EP14 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43765 | 43765 | 43765 |  | 43765 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43766 | EB105 Version | [6 empty] | 43766 | 43766 | 43766 |  | 43766 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43784 | EB105 Slave Type | [6 empty] | 43784 | 43784 | 43784 |  | 43784 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43785 | EB105 Compressor EP14 Size | [6 empty] | 43785 | 43785 | 43785 |  | 43785 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
43786 | EB105-EP15-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43786 | 43786 | 43786 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43787 | EB105-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43787 | 43787 | 43787 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43788 | EB105-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43788 | 43788 | 43788 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43789 | EB105-EP15-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43789 | 43789 | 43789 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43790 | EB105-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43790 | 43790 | 43790 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43791 | EB105-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43791 | 43791 | 43791 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43792 | EB105-EP15-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43792 | 43792 | 43792 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43793 | EB105-EP15-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43793 | 43793 | 43793 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43794 | EB105-EP15-BP8 Pressure Transmitter | [6 empty] | 43794 | 43794 | 43794 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43795 | EB105-EP15 Compressor State | On/Off | [5 empty] | 43795 | 43795 | 43795 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43796 | EB105-EP15 Compr. time to start | [6 empty] | 43796 | 43796 | 43796 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43797 | EB105-EP15 Relay status | [6 empty] | 43797 | 43797 | 43797 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43798 | EB105-EP15 Heat med. pump status | [6 empty] | 43798 | 43798 | 43798 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43799 | EB105-EP15 Brine pump status | [6 empty] | 43799 | 43799 | 43799 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43800 | EB105-EP15 Compressor starts | [6 empty] | 43800 | 43800 | 43800 | [5 empty] | u32 | 1 | 0 | 0 | 0 | R
43802 | EB105-EP15 Tot. op.time compr | [6 empty] | 43802 | 43802 | 43802 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43804 | EB105-EP15 Tot. HW op.time compr | [6 empty] | 43804 | 43804 | 43804 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43806 | EB105-EP15 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43806 | 43806 | 43806 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43807 | EB105-EP14-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43807 | 43807 | 43807 |  | 43807 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43808 | EB105-EP14-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43808 | 43808 | 43808 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43809 | EB105-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43809 | 43809 | 43809 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43810 | EB105-EP14-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43810 | 43810 | 43810 |  | 43810 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43811 | EB105-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43811 | 43811 | 43811 |  | 43811 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43812 | EB105-EP14-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43812 | 43812 | 43812 |  | 43812 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43813 | EB105-EP14-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43813 | 43813 | 43813 |  | 43813 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43814 | EB105-EP14-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43814 | 43814 | 43814 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43815 | EB105-EP14-BP8 Pressure Transmitter | [6 empty] | 43815 | 43815 | 43815 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43816 | EB105-EP14 Compressor State | On/Off | [5 empty] | 43816 | 43816 | 43816 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43817 | EB105-EP14 Compr. time to start | [6 empty] | 43817 | 43817 | 43817 |  | 43817 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43818 | EB105-EP14 Relay status | [6 empty] | 43818 | 43818 | 43818 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43819 | EB105-EP14 Heat med. pump status | [6 empty] | 43819 | 43819 | 43819 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43820 | EB105-EP14 Brine pump status | [6 empty] | 43820 | 43820 | 43820 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43821 | EB105-EP14 Compressor starts | [6 empty] | 43821 | 43821 | 43821 |  | 43821 |  |  |  | u32 | 1 | 0 | 9999999 | 0 | R
43823 | EB105-EP14 Tot. op.time compr | [6 empty] | 43823 | 43823 | 43823 |  | 43823 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43825 | EB105-EP14 Tot. HW op.time compr | [6 empty] | 43825 | 43825 | 43825 |  | 43825 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43827 | EB105-EP14 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43827 | 43827 | 43827 |  | 43827 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43828 | EB104 Version | [6 empty] | 43828 | 43828 | 43828 |  | 43828 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43846 | EB104 Slave Type | [6 empty] | 43846 | 43846 | 43846 |  | 43846 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43847 | EB104 Compressor EP14 Size | [6 empty] | 43847 | 43847 | 43847 |  | 43847 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
43848 | EB104-EP15-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43848 | 43848 | 43848 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43849 | EB104-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43849 | 43849 | 43849 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43850 | EB104-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43850 | 43850 | 43850 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43851 | EB104-EP15-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43851 | 43851 | 43851 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43852 | EB104-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43852 | 43852 | 43852 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43853 | EB104-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43853 | 43853 | 43853 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43854 | EB104-EP15-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43854 | 43854 | 43854 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43855 | EB104-EP15-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43855 | 43855 | 43855 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43856 | EB104-EP15-BP8 Pressure Transmitter | [6 empty] | 43856 | 43856 | 43856 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43857 | EB104-EP15 Compressor State | On/Off | [5 empty] | 43857 | 43857 | 43857 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43858 | EB104-EP15 Compr. time to start | [6 empty] | 43858 | 43858 | 43858 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43859 | EB104-EP15 Relay status | [6 empty] | 43859 | 43859 | 43859 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43860 | EB104-EP15 Heat med. pump status | [6 empty] | 43860 | 43860 | 43860 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43861 | EB104-EP15 Brine pump status | [6 empty] | 43861 | 43861 | 43861 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43862 | EB104-EP15 Compressor starts | [6 empty] | 43862 | 43862 | 43862 | [5 empty] | u32 | 1 | 0 | 0 | 0 | R
43864 | EB104-EP15 Tot. op.time compr | [6 empty] | 43864 | 43864 | 43864 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43866 | EB104-EP15 Tot. HW op.time compr | [6 empty] | 43866 | 43866 | 43866 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43868 | EB104-EP15 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43868 | 43868 | 43868 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43869 | EB104-EP14-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43869 | 43869 | 43869 |  | 43869 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43870 | EB104-EP14-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43870 | 43870 | 43870 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43871 | EB104-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43871 | 43871 | 43871 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43872 | EB104-EP14-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43872 | 43872 | 43872 |  | 43872 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43873 | EB104-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43873 | 43873 | 43873 |  | 43873 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43874 | EB104-EP14-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43874 | 43874 | 43874 |  | 43874 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43875 | EB104-EP14-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43875 | 43875 | 43875 |  | 43875 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43876 | EB104-EP14-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43876 | 43876 | 43876 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43877 | EB104-EP14-BP8 Pressure Transmitter | [6 empty] | 43877 | 43877 | 43877 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43878 | EB104-EP14 Compressor State | On/Off | [5 empty] | 43878 | 43878 | 43878 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43879 | EB104-EP14 Compr. time to start | [6 empty] | 43879 | 43879 | 43879 |  | 43879 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43880 | EB104-EP14 Relay status | [6 empty] | 43880 | 43880 | 43880 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43881 | EB104-EP14 Heat med. pump status | [6 empty] | 43881 | 43881 | 43881 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43882 | EB104-EP14 Brine pump status | [6 empty] | 43882 | 43882 | 43882 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43883 | EB104-EP14 Compressor starts | [6 empty] | 43883 | 43883 | 43883 |  | 43883 |  |  |  | u32 | 1 | 0 | 9999999 | 0 | R
43885 | EB104-EP14 Tot. op.time compr | [6 empty] | 43885 | 43885 | 43885 |  | 43885 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43887 | EB104-EP14 Tot. HW op.time compr | [6 empty] | 43887 | 43887 | 43887 |  | 43887 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43889 | EB104-EP14 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43889 | 43889 | 43889 |  | 43889 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43890 | EB103 Version | [6 empty] | 43890 | 43890 | 43890 |  | 43890 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43908 | EB103 Slave Type | [6 empty] | 43908 | 43908 | 43908 |  | 43908 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43909 | EB103 Compressor EP14 Size | [6 empty] | 43909 | 43909 | 43909 |  | 43909 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
43910 | EB103-EP15-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43910 | 43910 | 43910 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43911 | EB103-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43911 | 43911 | 43911 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43912 | EB103-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43912 | 43912 | 43912 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43913 | EB103-EP15-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43913 | 43913 | 43913 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43914 | EB103-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43914 | 43914 | 43914 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43915 | EB103-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43915 | 43915 | 43915 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43916 | EB103-EP15-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43916 | 43916 | 43916 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43917 | EB103-EP15-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43917 | 43917 | 43917 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43918 | EB103-EP15-BP8 Pressure Transmitter | [6 empty] | 43918 | 43918 | 43918 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43919 | EB103-EP15 Compressor State | On/Off | [5 empty] | 43919 | 43919 | 43919 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43920 | EB103-EP15 Compr. time to start | [6 empty] | 43920 | 43920 | 43920 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43921 | EB103-EP15 Relay status | [6 empty] | 43921 | 43921 | 43921 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43922 | EB103-EP15 Heat med. pump status | [6 empty] | 43922 | 43922 | 43922 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43923 | EB103-EP15 Brine pump status | [6 empty] | 43923 | 43923 | 43923 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43924 | EB103-EP15 Compressor starts | [6 empty] | 43924 | 43924 | 43924 | [5 empty] | u32 | 1 | 0 | 0 | 0 | R
43926 | EB103-EP15 Tot. op.time compr | [6 empty] | 43926 | 43926 | 43926 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43928 | EB103-EP15 Tot. HW op.time compr | [6 empty] | 43928 | 43928 | 43928 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43930 | EB103-EP15 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43930 | 43930 | 43930 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43931 | EB103-EP14-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43931 | 43931 | 43931 |  | 43931 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43932 | EB103-EP14-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43932 | 43932 | 43932 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43933 | EB103-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43933 | 43933 | 43933 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43934 | EB103-EP14-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43934 | 43934 | 43934 |  | 43934 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43935 | EB103-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43935 | 43935 | 43935 |  | 43935 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43936 | EB103-EP14-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43936 | 43936 | 43936 |  | 43936 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43937 | EB103-EP14-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43937 | 43937 | 43937 |  | 43937 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43938 | EB103-EP14-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43938 | 43938 | 43938 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43939 | EB103-EP14-BP8 Pressure Transmitter | [6 empty] | 43939 | 43939 | 43939 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43940 | EB103-EP14 Compressor State | On/Off | [5 empty] | 43940 | 43940 | 43940 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43941 | EB103-EP14 Compr. time to start | [6 empty] | 43941 | 43941 | 43941 |  | 43941 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43942 | EB103-EP14 Relay status | [6 empty] | 43942 | 43942 | 43942 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43943 | EB103-EP14 Heat med. pump status | [6 empty] | 43943 | 43943 | 43943 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43944 | EB103-EP14 Brine pump status | [6 empty] | 43944 | 43944 | 43944 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43945 | EB103-EP14 Compressor starts | [6 empty] | 43945 | 43945 | 43945 |  | 43945 |  |  |  | u32 | 1 | 0 | 9999999 | 0 | R
43947 | EB103-EP14 Tot. op.time compr | [6 empty] | 43947 | 43947 | 43947 |  | 43947 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43949 | EB103-EP14 Tot. HW op.time compr | [6 empty] | 43949 | 43949 | 43949 |  | 43949 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
43951 | EB103-EP14 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43951 | 43951 | 43951 |  | 43951 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43952 | EB102 Version | [6 empty] | 43952 | 43952 | 43952 |  | 43952 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
43970 | EB102 Slave Type | [6 empty] | 43970 | 43970 | 43970 |  | 43970 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
43971 | EB102 Compressor EP14 Size | [6 empty] | 43971 | 43971 | 43971 |  | 43971 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
43972 | EB102-EP15-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43972 | 43972 | 43972 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43973 | EB102-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43973 | 43973 | 43973 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43974 | EB102-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43974 | 43974 | 43974 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43975 | EB102-EP15-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43975 | 43975 | 43975 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43976 | EB102-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43976 | 43976 | 43976 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43977 | EB102-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43977 | 43977 | 43977 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43978 | EB102-EP15-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43978 | 43978 | 43978 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43979 | EB102-EP15-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 43979 | 43979 | 43979 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43980 | EB102-EP15-BP8 Pressure Transmitter | [6 empty] | 43980 | 43980 | 43980 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43981 | EB102-EP15 Compressor State | On/Off | [5 empty] | 43981 | 43981 | 43981 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43982 | EB102-EP15 Compr. time to start | [6 empty] | 43982 | 43982 | 43982 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
43983 | EB102-EP15 Relay status | [6 empty] | 43983 | 43983 | 43983 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43984 | EB102-EP15 Heat med. pump status | [6 empty] | 43984 | 43984 | 43984 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43985 | EB102-EP15 Brine pump status | [6 empty] | 43985 | 43985 | 43985 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
43986 | EB102-EP15 Compressor starts | [6 empty] | 43986 | 43986 | 43986 | [5 empty] | u32 | 1 | 0 | 0 | 0 | R
43988 | EB102-EP15 Tot. op.time compr | [6 empty] | 43988 | 43988 | 43988 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43990 | EB102-EP15 Tot. HW op.time compr | [6 empty] | 43990 | 43990 | 43990 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
43992 | EB102-EP15 Alarm number | The value indicates the most severe current alarm | [5 empty] | 43992 | 43992 | 43992 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
43993 | EB102-EP14-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 43993 | 43993 | 43993 |  | 43993 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43994 | EB102-EP14-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 43994 | 43994 | 43994 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43995 | EB102-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 43995 | 43995 | 43995 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43996 | EB102-EP14-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 43996 | 43996 | 43996 |  | 43996 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43997 | EB102-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 43997 | 43997 | 43997 |  | 43997 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43998 | EB102-EP14-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 43998 | 43998 | 43998 |  | 43998 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
43999 | EB102-EP14-BT17 Suction | Suction temperature, BT17 | [5 empty] | 43999 | 43999 | 43999 |  | 43999 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44000 | EB102-EP14-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 44000 | 44000 | 44000 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44001 | EB102-EP14-BP8 Pressure Transmitter | [6 empty] | 44001 | 44001 | 44001 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44002 | EB102-EP14 Compressor State | On/Off | [5 empty] | 44002 | 44002 | 44002 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44003 | EB102-EP14 Compr. time to start | [6 empty] | 44003 | 44003 | 44003 |  | 44003 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44004 | EB102-EP14 Relay status | [6 empty] | 44004 | 44004 | 44004 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
44005 | EB102-EP14 Heat med. pump status | [6 empty] | 44005 | 44005 | 44005 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44006 | EB102-EP14 Brine pump status | [6 empty] | 44006 | 44006 | 44006 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44007 | EB102-EP14 Compressor starts | [6 empty] | 44007 | 44007 | 44007 |  | 44007 |  |  |  | u32 | 1 | 0 | 9999999 | 0 | R
44009 | EB102-EP14 Tot. op.time compr | [6 empty] | 44009 | 44009 | 44009 |  | 44009 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
44011 | EB102-EP14 Tot. HW op.time compr | [6 empty] | 44011 | 44011 | 44011 |  | 44011 |  |  | h | u32 | 1 | 0 | 9999999 | 0 | R
44013 | EB102-EP14 Alarm number | The value indicates the most severe current alarm | [5 empty] | 44013 | 44013 | 44013 |  | 44013 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
44014 | EB101 Version | [6 empty] | 44014 | 44014 | 44014 | 44014 | 44014 | 44014 | 44014 |  | u16 | 1 | 0 | 0 | 0 | R
44032 | EB101 Slave Type | [6 empty] | 44032 | 44032 | 44032 | 44032 | 44032 | 44032 | 44032 |  | u8 | 1 | 0 | 0 | 0 | R
44033 | EB101 Compressor EP14 Size | [6 empty] | 44033 | 44033 | 44033 | 44033 | 44033 | 44033 | 44033 | kW | u8 | 1 | 0 | 0 | 0 | R
44034 | EB101-EP15-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 44034 | 44034 | 44034 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44035 | EB101-EP15-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 44035 | 44035 | 44035 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44036 | EB101-EP15-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 44036 | 44036 | 44036 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44037 | EB101-EP15-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 44037 | 44037 | 44037 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44038 | EB101-EP15-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 44038 | 44038 | 44038 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44039 | EB101-EP15-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 44039 | 44039 | 44039 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44040 | EB101-EP15-BT17 Suction | Suction temperature, BT17 | [5 empty] | 44040 | 44040 | 44040 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44041 | EB101-EP15-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 44041 | 44041 | 44041 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44042 | EB101-EP15-BP8 Pressure Transmitter | [6 empty] | 44042 | 44042 | 44042 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44043 | EB101-EP15 Compressor State | On/Off | [5 empty] | 44043 | 44043 | 44043 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44044 | EB101-EP15 Compr. time to start | [6 empty] | 44044 | 44044 | 44044 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44045 | EB101-EP15 Relay status | [6 empty] | 44045 | 44045 | 44045 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
44046 | EB101-EP15 Heat med. pump status | [6 empty] | 44046 | 44046 | 44046 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44047 | EB101-EP15 Brine pump status | [6 empty] | 44047 | 44047 | 44047 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44048 | EB101-EP15 Compressor starts | [6 empty] | 44048 | 44048 | 44048 | [5 empty] | u32 | 1 | 0 | 0 | 0 | R
44050 | EB101-EP15 Tot. op.time compr | [6 empty] | 44050 | 44050 | 44050 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
44052 | EB101-EP15 Tot. HW op.time compr | [6 empty] | 44052 | 44052 | 44052 |  |  |  |  | h | u32 | 1 | 0 | 0 | 0 | R
44054 | EB101-EP15 Alarm number | The value indicates the most severe current alarm | [5 empty] | 44054 | 44054 | 44054 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
44055 | EB101-EP14-BT3 Return Temp. | Return temperature, BT3 | [5 empty] | 44055 | 44055 | 44055 | 44055 | 44055 | 44055 | 44055 | °C | s16 | 10 | 0 | 0 | 0 | R
44056 | EB101-EP14-BT10 Brine In Temp | Brine in temperature, BT10 | [5 empty] | 44056 | 44056 | 44056 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44057 | EB101-EP14-BT11 Brine Out Temp | Brine out temperature, BT11 | [5 empty] | 44057 | 44057 | 44057 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44058 | EB101-EP14-BT12 Condensor Out | Condensor temperature, BT12 | [5 empty] | 44058 | 44058 | 44058 | 44058 | 44058 | 44058 | 44058 | °C | s16 | 10 | 0 | 0 | 0 | R
44059 | EB101-EP14-BT14 Hot Gas Temp | Hot gas temperature, BT14 | [5 empty] | 44059 | 44059 | 44059 | 44059 | 44059 | 44059 | 44059 | °C | s16 | 10 | 0 | 0 | 0 | R
44060 | EB101-EP14-BT15 Liquid Line | Liquid line temperature, BT15 | [5 empty] | 44060 | 44060 | 44060 | 44060 | 44060 | 44060 | 44060 | °C | s16 | 10 | 0 | 0 | 0 | R
44061 | EB101-EP14-BT17 Suction | Suction temperature, BT17 | [5 empty] | 44061 | 44061 | 44061 | 44061 | 44061 | 44061 | 44061 | °C | s16 | 10 | 0 | 0 | 0 | R
44062 | EB101-EP14-BT29 Cpr. Oil. Temp. | Compressor oil temperature, BT29 | [5 empty] | 44062 | 44062 | 44062 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44063 | EB101-EP14-BP8 Pressure Transmitter | [6 empty] | 44063 | 44063 | 44063 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44064 | EB101-EP14 Compressor State | On/Off | [5 empty] | 44064 | 44064 | 44064 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44065 | EB101-EP14 Compr. time to start | [6 empty] | 44065 | 44065 | 44065 | 44065 | 44065 | 44065 | 44065 |  | u8 | 1 | 0 | 0 | 0 | R
44066 | EB101-EP14 Relay status | [6 empty] | 44066 | 44066 | 44066 | [5 empty] | u16 | 1 | 0 | 0 | 0 | R
44067 | EB101-EP14 Heat med. pump status | [6 empty] | 44067 | 44067 | 44067 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44068 | EB101-EP14 Brine pump status | [6 empty] | 44068 | 44068 | 44068 |  |  |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44069 | EB101-EP14 Compressor starts | [6 empty] | 44069 | 44069 | 44069 | 44069 | 44069 | 44069 | 44069 |  | u32 | 1 | 0 | 9999999 | 0 | R
44071 | EB101-EP14 Tot. op.time compr | [6 empty] | 44071 | 44071 | 44071 | 44071 | 44071 | 44071 | 44071 | h | u32 | 1 | 0 | 9999999 | 0 | R
44073 | EB101-EP14 Tot. HW op.time compr | [6 empty] | 44073 | 44073 | 44073 | 44073 | 44073 | 44073 | 44073 | h | u32 | 1 | 0 | 9999999 | 0 | R
44075 | EB101-EP14 Alarm number | The value indicates the most severe current alarm | [5 empty] | 44075 | 44075 | 44075 | 44075 | 44075 | 44075 | 44075 |  | u16 | 1 | 0 | 0 | 0 | R
44116 | EB100-EP15 Alarm Number | The value indicates the most severe current alarm | [6 empty] | 44116 | 44116 | [5 empty] | s16 | 1 | 0 | 0 | 0 | R
44137 | EB100-EP14 Alarm Number | The value indicates the most severe current alarm | [6 empty] | 44137 | 44137 | [5 empty] | s16 | 1 | 0 | 0 | 0 | R
44138 | EB108-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44138 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44139 | EB108-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44139 |  | 44139 |  | 44139 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44151 | EB107-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44151 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44152 | EB107-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44152 |  | 44152 |  | 44152 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44164 | EB106-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44164 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44165 | EB106-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44165 |  | 44165 |  | 44165 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44177 | EB105-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44177 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44178 | EB105-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44178 |  | 44178 |  | 44178 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44190 | EB104-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44190 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44191 | EB104-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44191 |  | 44191 |  | 44191 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44203 | EB103-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44203 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44204 | EB103-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44204 |  | 44204 |  | 44204 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44216 | EB102-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44216 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44217 | EB102-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44217 |  | 44217 |  | 44217 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44229 | EB101-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44229 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44230 | EB101-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44230 |  | 44230 |  | 44230 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44242 | EB100-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [7 empty] | 44242 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44243 | EB100-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2, 5=External Request | [5 empty] | 44243 |  | 44243 |  | 44243 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44256 | Ext. Cooling Blocked | [10 empty] | 44256 | 44256 | 44256 |  | u8 | 1 | 0 | 0 | 0 | R
44258 | External supply air accessory relays | Indicates the status of the relays on the external supply air accessory. The information is binary encoded. B0: relay K1 (QN40 close signal). B1: relay K2 (QN40 open signal) |  |  | 44258 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
44266 | Cool Degree Minutes | [5 empty] | 44266 | 44266 | 44266 | 44266 | 44266 | 44266 | 44266 | 44266 |  | s16 | 10 | -30000 | 30000 | 0 | R/W
44267 | Calc. Cooling Supply S4 | Calculated supply temperature in cooling mode for the climate system |  |  |  |  | 44267 | 44267 | 44267 | 44267 | 44267 | 44267 | 44267 | 44267 | °C | s16 | 10 | 0 | 0 | 0 | R
44268 | Calc. Cooling Supply S3 | Calculated supply temperature in cooling mode for the climate system |  |  |  |  | 44268 | 44268 | 44268 | 44268 | 44268 | 44268 | 44268 | 44268 | °C | s16 | 10 | 0 | 0 | 0 | R
44269 | Calc. Cooling Supply S2 | Calculated supply temperature in cooling mode for the climate system |  |  |  |  | 44269 | 44269 | 44269 | 44269 | 44269 | 44269 | 44269 | 44269 | °C | s16 | 10 | 0 | 0 | 0 | R
44270 | Calc. Cooling Supply S1 | Calculated supply temperature in cooling mode for the climate system |  |  |  |  | 44270 | 44270 | 44270 | 44270 | 44270 | 44270 | 44270 | 44270 | °C | s16 | 10 | 0 | 0 | 0 | R
44276 | State ACS | The state of the ACS accessory |  |  |  |  | 44276 | 44276 | 44276 | 44276 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44277 | EQ1-QN25 State ACS Heat Dump | 10=shunt off,20=shunt open,30=shunt closed |  |  |  |  | 44277 | 44277 | 44277 | 44277 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44278 | EQ1-QN18 State ACS Cool Dump | 10=shunt off,20=shunt open,30=shunt closed |  |  |  |  | 44278 | 44278 | 44278 | 44278 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44282 | Used cprs. HW | The number of compressors that's currently producing hot water |  |  |  | 44282 |  | 44282 | 44282 | 44282 |  | 44282 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44283 | Used cprs. heat | The number of compressors that's currently producing heating |  |  |  | 44283 |  | 44283 | 44283 | 44283 |  | 44283 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44284 | Used cprs. pool 1 | The number of compressors that's currently producing poolheating for pool 1 | [5 empty] | 44284 | 44284 | 44284 |  | 44284 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44285 | Used cprs. pool 2 | The number of compressors that's currently producing poolheating for pool 2 | [5 empty] | 44285 | 44285 | 44285 |  | 44285 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44298 | Heat Meter - HW Cpr and Add EP14 | Accumulated energy production as calculated by the heat meter | 44298 | 44298 | 44298 | 44298 | 44298 | 44298 | 44298 | 44298 |  |  | 44298 | 44298 | kWh | u32 | 10 | 0 | 0 | 0 | R
44300 | Heat Meter - Heat Cpr and Add EP14 | Accumulated energy production as calculated by the heat meter | 44300 | 44300 | 44300 | 44300 | 44300 | 44300 | 44300 | 44300 |  |  | 44300 | 44300 | kWh | u32 | 10 | 0 | 0 | 0 | R
44302 | Heat Meter - Cooling Cpr EP14 | Accumulated energy production as calculated by the heat meter |  |  |  |  | 44302 | 44302 | 44302 | 44302 |  |  | 44302 | 44302 | kWh | u32 | 10 | 0 | 0 | 0 | R
44304 | Heat Meter - Pool Cpr EP14 | Accumulated energy production as calculated by the heat meter |  |  | 44304 | 44304 | 44304 | 44304 | 44304 | 44304 |  |  | 44304 | 44304 | kWh | u32 | 10 | 0 | 0 | 0 | R
44306 | Heat Meter - HW Cpr EP14 | Accumulated energy production as calculated by the heat meter |  |  | 44306 | 44306 | 44306 | 44306 | 44306 | 44306 |  |  | 44306 | 44306 | kWh | u32 | 10 | 0 | 0 | 0 | R
44308 | Heat Meter - Heat Cpr EP14 | Accumulated energy production as calculated by the heat meter |  |  | 44308 | 44308 | 44308 | 44308 | 44308 | 44308 |  |  | 44308 | 44308 | kWh | u32 | 10 | 0 | 0 | 0 | R
44317 | SCA accessory relays | Indicates the status of the relays on the SCA accessory. The information is binary encoded. B0: relay K1 (Solar pump). B1: relay K2 (Solar Cooling Pump) B2: relay K3 (QN28) |  |  | 44317 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
44320 | Used cprs. cool | The number of compressors that's currently producing active cooling | [5 empty] | 44320 | 44320 | 44320 |  | 44320 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44322 | Speed ext cooling pump GP12 | [11 empty] | 44322 | 44322 | % | u8 | 1 | 0 | 0 | 0 | R
44323 | Cooling pump manual speed | Cooling pump speed if manual | [10 empty] | 44323 | 44323 | % | s8 | 1 | 1 | 100 | 70 | R/W
44331 | Software release |  | 44331 | 44331 | 44331 | 44331 | 44331 | 44331 | 44331 | 44331 | 44331 | 44331 | 44331 | 44331 |  | u8 | 1 | 0 | 0 | 0 | R
44334 | EB108-EP14-BT28 Outdoor Temp | Current outdoor temperature, BT28 | [9 empty] | 44334 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44335 | EB108-EP14-BT16 Evaporator | Evaporator temperature, BT16 | [9 empty] | 44335 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44338 | EB107-EP14-BT28 Outdoor Temp | Current outdoor temperature, BT28 | [9 empty] | 44338 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44339 | EB107-EP14-BT16 Evaporator | Evaporator temperature, BT16 | [9 empty] | 44339 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44342 | EB106-EP14-BT28 Outdoor Temp | Current outdoor temperature, BT28 | [9 empty] | 44342 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44343 | EB106-EP14-BT16 Evaporator | Evaporator temperature, BT16 | [9 empty] | 44343 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44346 | EB105-EP14-BT28 Outdoor Temp | Current outdoor temperature, BT28 | [9 empty] | 44346 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44347 | EB105-EP14-BT16 Evaporator | Evaporator temperature, BT16 | [9 empty] | 44347 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44350 | EB104-EP14-BT28 Outdoor Temp | Current outdoor temperature, BT28 | [9 empty] | 44350 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44351 | EB104-EP14-BT16 Evaporator | Evaporator temperature, BT16 | [9 empty] | 44351 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44354 | EB103-EP14-BT28 Outdoor Temp | Current outdoor temperature, BT28 | [9 empty] | 44354 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44355 | EB103-EP14-BT16 Evaporator | Evaporator temperature, BT16 | [9 empty] | 44355 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44358 | EB102-EP14-BT28 Outdoor Temp | Current outdoor temperature, BT28 | [9 empty] | 44358 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44359 | EB102-EP14-BT16 Evaporator | Evaporator temperature, BT16 | [9 empty] | 44359 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44362 | EB101-EP14-BT28 Outdoor Temp | Current outdoor temperature, BT28 | [8 empty] | 44362 | 44362 | 44362 | 44362 | °C | s16 | 10 | 0 | 0 | 0 | R
44363 | EB101-EP14-BT16 Evaporator | Evaporator temperature, BT16 | [8 empty] | 44363 | 44363 | 44363 | 44363 | °C | s16 | 10 | 0 | 0 | 0 | R
44379 | Ext. Addition Pump | On/Off | [11 empty] | 44379 |  | u8 | 1 | 0 | 0 | 0 | R
44380 | Docked External Compressors | Number of compressors with external control | [5 empty] | 44380 | 44380 | 44380 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44389 | EB108 Speed charge pump | [10 empty] | 44389 |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44390 | EB107 Speed charge pump | [10 empty] | 44390 |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44391 | EB106 Speed charge pump | [10 empty] | 44391 |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44392 | EB105 Speed charge pump | [10 empty] | 44392 |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44393 | EB104 Speed charge pump | [10 empty] | 44393 |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44394 | EB103 Speed charge pump | [10 empty] | 44394 |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44395 | EB102 Speed charge pump | [10 empty] | 44395 |  |  | % | u8 | 1 | 0 | 0 | 0 | R
44396 | EB101 Speed charge pump | [9 empty] | 44396 | 44396 | 44396 | 44396 | % | u8 | 1 | 0 | 0 | 0 | R
44410 | EB108 Bit Register | [6 empty] | 44410 | 44410 | 44410 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44411 | EB108-BT6 Hot water load temp. | [6 empty] | 44411 | 44411 | 44411 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44412 | EB108-BT7 Hot water top temp. | [6 empty] | 44412 | 44412 | 44412 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44413 | EB108-BT2 Supply temp. | [6 empty] | 44413 | 44413 | 44413 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44414 | EB108-EP15 Compressor State | On/Off | [7 empty] | 44414 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44415 | EB108-EP14 Compressor State | On/Off | [7 empty] | 44415 |  | 44415 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44416 | EB107 Bit Register | [6 empty] | 44416 | 44416 | 44416 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44417 | EB107-BT6 Hot water load temp. | [6 empty] | 44417 | 44417 | 44417 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44418 | EB107-BT7 Hot water top temp. | [6 empty] | 44418 | 44418 | 44418 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44419 | EB107-BT2 Supply temp. | [6 empty] | 44419 | 44419 | 44419 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44420 | EB107-EP15 Compressor State | On/Off | [7 empty] | 44420 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44421 | EB107-EP14 Compressor State | On/Off | [5 empty] | 44421 | 44421 | 44421 |  | 44421 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44422 | EB106 Bit Register | [6 empty] | 44422 | 44422 | 44422 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44423 | EB106-BT6 Hot water load temp. | [6 empty] | 44423 | 44423 | 44423 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44424 | EB106-BT7 Hot water top temp. | [6 empty] | 44424 | 44424 | 44424 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44425 | EB106-BT2 Supply temp. | [6 empty] | 44425 | 44425 | 44425 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44426 | EB106-EP15 Compressor State | On/Off | [7 empty] | 44426 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44427 | EB106-EP14 Compressor State | On/Off | [7 empty] | 44427 |  | 44427 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44428 | EB105 Bit Register | [6 empty] | 44428 | 44428 | 44428 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44429 | EB105-BT6 Hot water load temp. | [6 empty] | 44429 | 44429 | 44429 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44430 | EB105-BT7 Hot water top temp. | [6 empty] | 44430 | 44430 | 44430 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44431 | EB105-BT2 Supply temp. | [6 empty] | 44431 | 44431 | 44431 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44432 | EB105-EP15 Compressor State | On/Off | [7 empty] | 44432 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44433 | EB105-EP14 Compressor State | On/Off | [7 empty] | 44433 |  | 44433 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44434 | EB104 Bit Register | [6 empty] | 44434 | 44434 | 44434 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44435 | EB104-BT6 Hot water load temp. | [6 empty] | 44435 | 44435 | 44435 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44436 | EB104-BT7 Hot water top temp. | [6 empty] | 44436 | 44436 | 44436 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44437 | EB104-BT2 Supply temp. | [6 empty] | 44437 | 44437 | 44437 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44438 | EB104-EP15 Compressor State | On/Off | [7 empty] | 44438 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44439 | EB104-EP14 Compressor State | On/Off | [7 empty] | 44439 |  | 44439 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44440 | EB103 Bit Register | [6 empty] | 44440 | 44440 | 44440 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44441 | EB103-BT6 Hot water load temp. | [6 empty] | 44441 | 44441 | 44441 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44442 | EB103-BT7 Hot water top temp. | [6 empty] | 44442 | 44442 | 44442 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44443 | EB103-BT2 Supply temp. | [6 empty] | 44443 | 44443 | 44443 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44444 | EB103-EP15 Compressor State | On/Off | [7 empty] | 44444 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44445 | EB103-EP14 Compressor State | On/Off | [7 empty] | 44445 |  | 44445 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44446 | EB102 Bit Register | [6 empty] | 44446 | 44446 | 44446 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44447 | EB102-BT6 Hot water load temp. | [6 empty] | 44447 | 44447 | 44447 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44448 | EB102-BT7 Hot water top temp. | [6 empty] | 44448 | 44448 | 44448 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44449 | EB102-BT2 Supply temp. | [6 empty] | 44449 | 44449 | 44449 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44450 | EB102-EP15 Compressor State | On/Off | [7 empty] | 44450 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44451 | EB102-EP14 Compressor State | On/Off | [7 empty] | 44451 |  | 44451 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44452 | EB101 Bit Register | [6 empty] | 44452 | 44452 | 44452 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44453 | EB101-BT6 Hot water load temp. | [6 empty] | 44453 | 44453 | 44453 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44454 | EB101-BT7 Hot water top temp. | [6 empty] | 44454 | 44454 | 44454 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44455 | EB101-BT2 Supply temp. | [6 empty] | 44455 | 44455 | 44455 |  |  |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44456 | EB101-EP15 Compressor State | On/Off | [7 empty] | 44456 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44457 | EB101-EP14 Compressor State | On/Off | [7 empty] | 44457 | 44457 | 44457 | 44457 | 44457 |  | u8 | 1 | 0 | 0 | 0 | R
44483 | State of the extra additional heat in series | 0 = Off, 1 = On | [8 empty] | 44483 | 44483 | 44483 | 44483 |  | u8 | 1 | 0 | 0 | 0 | R
44487 | Docked Cool Compressors | Number of compressors docked to cooling | [5 empty] | 44487 | 44487 | 44487 | 44487 | 44487 | 44487 | 44487 |  | u8 | 1 | 0 | 0 | 0 | R
44503 | EB108-EP14 High Pressure Sensor Outdoor Unit | [10 empty] | 44503 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44504 | EB108-EP14 Low Pressure Sensor Outdoor Unit | [10 empty] | 44504 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44505 | EB108-EP14 Actual Cpr Frequency Outdoor Unit | [10 empty] | 44505 |  |  | Hz | s16 | 10 | 0 | 0 | 0 | R
44506 | EB108-EP14 Protection Status Register Outdoor Unit | [10 empty] | 44506 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
44507 | EB108-EP14 Defrosting Outdoor Unit | 0=No, 1=Active, 2 = Passive | [9 empty] | 44507 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44510 | EB108-EP14 Calculated Power Outdoor Unit | [10 empty] | 44510 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
44531 | EB107-EP14 High Pressure Sensor Outdoor Unit | [10 empty] | 44531 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44532 | EB107-EP14 Low Pressure Sensor Outdoor Unit | [10 empty] | 44532 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44533 | EB107-EP14 Actual Cpr Frequency Outdoor Unit | [10 empty] | 44533 |  |  | Hz | s16 | 10 | 0 | 0 | 0 | R
44534 | EB107-EP14 Protection Status Register Outdoor Unit | [10 empty] | 44534 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
44535 | EB107-EP14 Defrosting Outdoor Unit | 0=No, 1=Active, 2 = Passive | [9 empty] | 44535 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44538 | EB107-EP14 Calculated Power Outdoor Unit | [10 empty] | 44538 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
44559 | EB106-EP14 High Pressure Sensor Outdoor Unit | [10 empty] | 44559 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44560 | EB106-EP14 Low Pressure Sensor Outdoor Unit | [10 empty] | 44560 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44561 | EB106-EP14 Actual Cpr Frequency Outdoor Unit | [10 empty] | 44561 |  |  | Hz | s16 | 10 | 0 | 0 | 0 | R
44562 | EB106-EP14 Protection Status Register Outdoor Unit | [10 empty] | 44562 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
44563 | EB106-EP14 Defrosting Outdoor Unit | 0=No, 1=Active, 2 = Passive | [9 empty] | 44563 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44566 | EB106-EP14 Calculated Power Outdoor Unit | [10 empty] | 44566 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
44587 | EB105-EP14 High Pressure Sensor Outdoor Unit | [10 empty] | 44587 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44588 | EB105-EP14 Low Pressure Sensor Outdoor Unit | [10 empty] | 44588 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44589 | EB105-EP14 Actual Cpr Frequency Outdoor Unit | [10 empty] | 44589 |  |  | Hz | s16 | 10 | 0 | 0 | 0 | R
44590 | EB105-EP14 Protection Status Register Outdoor Unit | [10 empty] | 44590 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
44591 | EB105-EP14 Defrosting Outdoor Unit | 0=No, 1=Active, 2 = Passive | [9 empty] | 44591 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44594 | EB105-EP14 Calculated Power Outdoor Unit | [10 empty] | 44594 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
44615 | EB104-EP14 High Pressure Sensor Outdoor Unit | [10 empty] | 44615 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44616 | EB104-EP14 Low Pressure Sensor Outdoor Unit | [10 empty] | 44616 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44617 | EB104-EP14 Actual Cpr Frequency Outdoor Unit | [10 empty] | 44617 |  |  | Hz | s16 | 10 | 0 | 0 | 0 | R
44618 | EB104-EP14 Protection Status Register Outdoor Unit | [10 empty] | 44618 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
44619 | EB104-EP14 Defrosting Outdoor Unit | 0=No, 1=Active, 2 = Passive | [9 empty] | 44619 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44622 | EB104-EP14 Calculated Power Outdoor Unit | [10 empty] | 44622 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
44643 | EB103-EP14 High Pressure Sensor Outdoor Unit | [10 empty] | 44643 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44644 | EB103-EP14 Low Pressure Sensor Outdoor Unit | [10 empty] | 44644 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44645 | EB103-EP14 Actual Cpr Frequency Outdoor Unit | [10 empty] | 44645 |  |  | Hz | s16 | 10 | 0 | 0 | 0 | R
44646 | EB103-EP14 Protection Status Register Outdoor Unit | [10 empty] | 44646 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
44647 | EB103-EP14 Defrosting Outdoor Unit | 0=No, 1=Active, 2 = Passive | [9 empty] | 44647 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44650 | EB103-EP14 Calculated Power Outdoor Unit | [10 empty] | 44650 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
44671 | EB102-EP14 High Pressure Sensor Outdoor Unit | [10 empty] | 44671 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44672 | EB102-EP14 Low Pressure Sensor Outdoor Unit | [10 empty] | 44672 |  |  | bar | s16 | 10 | 0 | 0 | 0 | R
44673 | EB102-EP14 Actual Cpr Frequency Outdoor Unit | [10 empty] | 44673 |  |  | Hz | s16 | 10 | 0 | 0 | 0 | R
44674 | EB102-EP14 Protection Status Register Outdoor Unit | [10 empty] | 44674 |  |  |  | u16 | 1 | 0 | 0 | 0 | R
44675 | EB102-EP14 Defrosting Outdoor Unit | 0=No, 1=Active, 2 = Passive | [9 empty] | 44675 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44678 | EB102-EP14 Calculated Power Outdoor Unit | [10 empty] | 44678 |  |  | kW | u8 | 1 | 0 | 0 | 0 | R
44699 | EB101-EP14 High Pressure Sensor Outdoor Unit | [9 empty] | 44699 | 44699 | 44699 | 44699 | bar | s16 | 10 | 0 | 0 | 0 | R
44700 | EB101-EP14 Low Pressure Sensor Outdoor Unit | [9 empty] | 44700 | 44700 | 44700 | 44700 | bar | s16 | 10 | 0 | 0 | 0 | R
44701 | EB101-EP14 Actual Cpr Frequency Outdoor Unit | [9 empty] | 44701 | 44701 | 44701 | 44701 | Hz | s16 | 10 | 0 | 0 | 0 | R
44702 | EB101-EP14 Protection Status Register Outdoor Unit | [9 empty] | 44702 | 44702 | 44702 | 44702 |  | u16 | 1 | 0 | 0 | 0 | R
44703 | EB101-EP14 Defrosting Outdoor Unit | 0=No, 1=Active, 2 = Passive | [8 empty] | 44703 | 44703 | 44703 | 44703 |  | u8 | 1 | 0 | 0 | 0 | R
44706 | EB101-EP14 Calculated Power Outdoor Unit | [9 empty] | 44706 | 44706 | 44706 | 44706 | kW | u8 | 1 | 0 | 0 | 0 | R
44742 | HW valve QN35 | [12 empty] | 44742 |  | u8 | 1 | 0 | 0 | 0 | R
44743 | Internal charge pump | [11 empty] | 44743 | 44743 |  | u8 | 1 | 0 | 0 | 0 | R
44744 | Extra heating system pump S4 |  | 44744 | 44744 | 44744 | 44744 | 44744 | 44744 | 44744 | 44744 |  | 44744 | 44744 | 44744 |  | u8 | 1 | 0 | 0 | 0 | R
44745 | Extra heating system pump S3 |  | 44745 | 44745 | 44745 | 44745 | 44745 | 44745 | 44745 | 44745 |  | 44745 | 44745 | 44745 |  | u8 | 1 | 0 | 0 | 0 | R
44746 | Extra heating system pump S2 |  | 44746 | 44746 | 44746 | 44746 | 44746 | 44746 | 44746 | 44746 |  | 44746 | 44746 | 44746 |  | u8 | 1 | 0 | 0 | 0 | R
44748 | Pool 2 Pump Status | 1=on,0=off |  |  |  |  | 44748 | 44748 | 44748 | 44748 |  | 44748 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44749 | Pool 1 Pump Status | 1=on,0=off |  |  |  |  | 44749 | 44749 | 44749 | 44749 |  | 44749 | 44749 | 44749 |  | u8 | 1 | 0 | 0 | 0 | R
44750 | FJVM pump |  | 44750 | 44750 | [11 empty] | u8 | 1 | 0 | 0 | 0 | R
44751 | EQ1-QN12 ACS Valve | ACS valve is 1=open,0=closed |  |  |  |  | 44751 | 44751 | 44751 | 44751 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44752 | EQ1-GP20 ACS Dump Signal | GP20 is 1=running,0=off |  |  |  |  | 44752 | 44752 | 44752 | 44752 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44753 | Passive Cool Shunt | [5 empty] | 44753 | 44753 | 44753 | 44753 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44754 | GP13 Passive Cool Pool | [5 empty] | 44754 | 44754 | 44754 | 44754 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44755 | DEW hot water valve |  |  |  | 44755 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
44756 | State ground water pump | [5 empty] | 44756 | 44756 | 44756 | 44756 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44757 | SCA hot water valve |  |  |  | 44757 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R
44761 | EB108-EP14 calc. ou compressor freq | Calculated compressor frequency | [9 empty] | 44761 |  |  | Hz | u8 | 1 | 0 | 0 | 0 | R
44763 | EB107-EP14 calc. ou compressor freq | Calculated compressor frequency | [9 empty] | 44763 |  |  | Hz | u8 | 1 | 0 | 0 | 0 | R
44765 | EB106-EP14 calc. ou compressor freq | Calculated compressor frequency | [9 empty] | 44765 |  |  | Hz | u8 | 1 | 0 | 0 | 0 | R
44767 | EB105-EP14 calc. ou compressor freq | Calculated compressor frequency | [9 empty] | 44767 |  |  | Hz | u8 | 1 | 0 | 0 | 0 | R
44769 | EB104-EP14 calc. ou compressor freq | Calculated compressor frequency | [9 empty] | 44769 |  |  | Hz | u8 | 1 | 0 | 0 | 0 | R
44771 | EB103-EP14 calc. ou compressor freq | Calculated compressor frequency | [9 empty] | 44771 |  |  | Hz | u8 | 1 | 0 | 0 | 0 | R
44773 | EB102-EP14 calc. ou compressor freq | Calculated compressor frequency | [9 empty] | 44773 |  |  | Hz | u8 | 1 | 0 | 0 | 0 | R
44775 | EB101-EP14 calc. ou compressor freq | Calculated compressor frequency | [8 empty] | 44775 | 44775 | 44775 | 44775 | Hz | u8 | 1 | 0 | 0 | 0 | R
44778 | EP10-QN41 State Brine Shunt | 10=shunt off,20=shunt open,30=shunt closed | [6 empty] | 44778 | 44778 | [5 empty] | u8 | 1 | 0 | 0 | 0 | R
44824 | EB108-EP14 Current Sensor | [10 empty] | 44824 |  |  |  | s16 | 10 | 0 | 0 | 0 | R
44825 | EB108-EP14 Hz Down Mode Outdoor Unit | 0=No, 1=Yes | [9 empty] | 44825 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44830 | EB107-EP14 Current Sensor | [10 empty] | 44830 |  |  |  | s16 | 10 | 0 | 0 | 0 | R
44831 | EB107-EP14 Hz Down Mode Outdoor Unit | 0=No, 1=Yes | [9 empty] | 44831 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44836 | EB106-EP14 Current Sensor | [10 empty] | 44836 |  |  |  | s16 | 10 | 0 | 0 | 0 | R
44837 | EB106-EP14 Hz Down Mode Outdoor Unit | 0=No, 1=Yes | [9 empty] | 44837 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44842 | EB105-EP14 Current Sensor | [10 empty] | 44842 |  |  |  | s16 | 10 | 0 | 0 | 0 | R
44843 | EB105-EP14 Hz Down Mode Outdoor Unit | 0=No, 1=Yes | [9 empty] | 44843 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44848 | EB104-EP14 Current Sensor | [10 empty] | 44848 |  |  |  | s16 | 10 | 0 | 0 | 0 | R
44849 | EB104-EP14 Hz Down Mode Outdoor Unit | 0=No, 1=Yes | [9 empty] | 44849 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44854 | EB103-EP14 Current Sensor | [10 empty] | 44854 |  |  |  | s16 | 10 | 0 | 0 | 0 | R
44855 | EB103-EP14 Hz Down Mode Outdoor Unit | 0=No, 1=Yes | [9 empty] | 44855 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44860 | EB102-EP14 Current Sensor | [10 empty] | 44860 |  |  |  | s16 | 10 | 0 | 0 | 0 | R
44861 | EB102-EP14 Hz Down Mode Outdoor Unit | 0=No, 1=Yes | [9 empty] | 44861 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44866 | EB101-EP14 Current Sensor | [9 empty] | 44866 | 44866 | 44866 | 44866 |  | s16 | 10 | 0 | 0 | 0 | R
44867 | EB101-EP14 Hz Down Mode Outdoor Unit | 0=No, 1=Yes | [8 empty] | 44867 | 44867 | 44867 | 44867 |  | u8 | 1 | 0 | 0 | 0 | R
44874 | State SG Ready |  | 44874 | 44874 | 44874 | 44874 | 44874 | 44874 | 44874 | 44874 | 44874 | 44874 | 44874 | 44874 |  | u8 | 1 | 0 | 0 | 0 | R
44878 | SG Ready input A |  | 44878 | 44878 | 44878 | 44878 | 44878 | 44878 | 44878 | 44878 | 44878 | 44878 | 44878 | 44878 |  | u8 | 1 | 0 | 0 | 0 | R
44879 | SG Ready input B |  | 44879 | 44879 | 44879 | 44879 | 44879 | 44879 | 44879 | 44879 | 44879 | 44879 | 44879 | 44879 |  | u8 | 1 | 0 | 0 | 0 | R
44896 | Smart Price Adaption Heating Offset |  | 44896 | 44896 | 44896 | 44896 | 44896 | 44896 | 44896 | 44896 | 44896 | 44896 | 44896 | 44896 |  | s8 | 10 | 0 | 0 | 0 | R
44897 | Smart Price Adaption HW Comfort Mode | 0=Eco,1=Normal,2=Luxury,10=Normal+,20=Mini | 44897 | 44897 | 44897 | 44897 | 44897 | 44897 | 44897 | 44897 | 44897 | 44897 | 44897 | 44897 |  | s8 | 1 | 0 | 0 | 0 | R
44898 | Smart Price Adaption Pool Offset |  | 44898 | 44898 | 44898 | 44898 | 44898 | 44898 | 44898 | 44898 | 44898 | 44898 | 44898 | 44898 |  | s8 | 1 | 0 | 0 | 0 | R
44899 | Smart Price Adaption Cool Offset |  | 44899 | 44899 | 44899 | 44899 | 44899 | 44899 | 44899 | 44899 | 44899 | 44899 | 44899 | 44899 |  | s8 | 1 | 0 | 0 | 0 | R
44908 | State smart price adaption |  | 44908 | 44908 | 44908 | 44908 | 44908 | 44908 | 44908 | 44908 | 44908 | 44908 | 44908 | 44908 |  | u8 | 1 | 0 | 0 | 0 | R
44910 | Brine Pump dT Actual | Current value between set and act value on brine pumps |  |  |  |  | 44910 | 44910 | 44910 | 44910 | [5 empty] | s16 | 10 | 0 | 0 | 0 | R
44911 | Brine Pump dT Set Point | Set point delta T for the brine pumps |  |  |  |  | 44911 | 44911 | 44911 | 44911 | [5 empty] | s16 | 10 | 0 | 0 | 0 | R
44935 | EB108-EP14-BT16 Evaporator 2 | Evaporator 2 temperature, BT16 | [9 empty] | 44935 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44936 | EB108-EP14 Inverter Temperature | Inverter temperature | [9 empty] | 44936 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44937 | EB108-EP14-Fan Speed Step | [10 empty] | 44937 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44941 | EB107-EP14-BT16 Evaporator 2 | Evaporator 2 temperature, BT16 | [9 empty] | 44941 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44942 | EB107-EP14 Inverter Temperature | Inverter temperature | [9 empty] | 44942 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44943 | EB107-EP14-Fan Speed Step | [10 empty] | 44943 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44947 | EB106-EP14-BT16 Evaporator 2 | Evaporator 2 temperature, BT16 | [9 empty] | 44947 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44948 | EB106-EP14 Inverter Temperature | Inverter temperature | [9 empty] | 44948 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44949 | EB106-EP14-Fan Speed Step | [10 empty] | 44949 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44953 | EB105-EP14-BT16 Evaporator 2 | Evaporator 2 temperature, BT16 | [9 empty] | 44953 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44954 | EB105-EP14 Inverter Temperature | Inverter temperature | [9 empty] | 44954 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44955 | EB105-EP14-Fan Speed Step | [10 empty] | 44955 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44959 | EB104-EP14-BT16 Evaporator 2 | Evaporator 2 temperature, BT16 | [9 empty] | 44959 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44960 | EB104-EP14 Inverter Temperature | Inverter temperature | [9 empty] | 44960 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44961 | EB104-EP14-Fan Speed Step | [10 empty] | 44961 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44965 | EB103-EP14-BT16 Evaporator 2 | Evaporator 2 temperature, BT16 | [9 empty] | 44965 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44966 | EB103-EP14 Inverter Temperature | Inverter temperature | [9 empty] | 44966 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44967 | EB103-EP14-Fan Speed Step | [10 empty] | 44967 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44971 | EB102-EP14-BT16 Evaporator 2 | Evaporator 2 temperature, BT16 | [9 empty] | 44971 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44972 | EB102-EP14 Inverter Temperature | Inverter temperature | [9 empty] | 44972 |  |  | °C | s16 | 10 | 0 | 0 | 0 | R
44973 | EB102-EP14-Fan Speed Step | [10 empty] | 44973 |  |  |  | u8 | 1 | 0 | 0 | 0 | R
44977 | EB101-EP14-BT16 Evaporator 2 | Evaporator 2 temperature, BT16 | [8 empty] | 44977 | 44977 | 44977 | 44977 | °C | s16 | 10 | 0 | 0 | 0 | R
44978 | EB101-EP14 Inverter Temperature | Inverter temperature | [8 empty] | 44978 | 44978 | 44978 | 44978 | °C | s16 | 10 | 0 | 0 | 0 | R
44979 | EB101-EP14-Fan Speed Step | [9 empty] | 44979 | 44979 | 44979 | 44979 |  | u8 | 1 | 0 | 0 | 0 | R
45001 | Alarm | Indicates the alarm number of the most severe current alarm | 45001 | 45001 | 45001 | 45001 | 45001 | 45001 | 45001 | 45001 | 45001 | 45001 | 45001 | 45001 |  | s16 | 1 | 0 | 0 | 0 | R
45171 | Alarm Reset | Reset alarm by setting value 1 | 45171 | 45171 | 45171 | 45171 | 45171 | 45171 | 45171 | 45171 | 45171 | 45171 | 45171 | 45171 |  | u8 | 1 | 0 | 0 | 0 | R/W
47004 | Heat Curve S4 | Heat curve, see manual for more information | 47004 | 47004 | 47004 | 47004 | 47004 | 47004 | 47004 | 47004 |  | 47004 | 47004 | 47004 |  | s8 | 1 | 0 | 15 | 9 | R/W
47005 | Heat Curve S3 | Heat curve, see manual for more information | 47005 | 47005 | 47005 | 47005 | 47005 | 47005 | 47005 | 47005 |  | 47005 | 47005 | 47005 |  | s8 | 1 | 0 | 15 | 9 | R/W
47006 | Heat Curve S2 | Heat curve, see manual for more information | 47006 | 47006 | 47006 | 47006 | 47006 | 47006 | 47006 | 47006 |  | 47006 | 47006 | 47006 |  | s8 | 1 | 0 | 15 | 9 | R/W
47007 | Heat Curve S1 | Heat curve, see manual for more information | 47007 | 47007 | 47007 | 47007 | 47007 | 47007 | 47007 | 47007 | 47007 | 47007 | 47007 | 47007 |  | s8 | 1 | 0 | 15 | 9 | R/W
47008 | Heat Offset S4 | Offset of the heat curve, see manual for more information | 47008 | 47008 | 47008 | 47008 | 47008 | 47008 | 47008 | 47008 |  | 47008 | 47008 | 47008 |  | s8 | 1 | -10 | 10 | 0 | R/W
47009 | Heat Offset S3 | Offset of the heat curve, see manual for more information | 47009 | 47009 | 47009 | 47009 | 47009 | 47009 | 47009 | 47009 |  | 47009 | 47009 | 47009 |  | s8 | 1 | -10 | 10 | 0 | R/W
47010 | Heat Offset S2 | Offset of the heat curve, see manual for more information | 47010 | 47010 | 47010 | 47010 | 47010 | 47010 | 47010 | 47010 |  | 47010 | 47010 | 47010 |  | s8 | 1 | -10 | 10 | 0 | R/W
47011 | Heat Offset S1 | Offset of the heat curve, see manual for more information | 47011 | 47011 | 47011 | 47011 | 47011 | 47011 | 47011 | 47011 | 47011 | 47011 | 47011 | 47011 |  | s8 | 1 | -10 | 10 | 0 | R/W
47012 | Min Supply System 4 |  | 47012 | 47012 | 47012 | 47012 | 47012 | 47012 | 47012 | 47012 |  | 47012 | 47012 | 47012 | °C | s16 | 10 | 50 | 700 | 200 | R/W
47013 | Min Supply System 3 |  | 47013 | 47013 | 47013 | 47013 | 47013 | 47013 | 47013 | 47013 |  | 47013 | 47013 | 47013 | °C | s16 | 10 | 50 | 700 | 200 | R/W
47014 | Min Supply System 2 |  | 47014 | 47014 | 47014 | 47014 | 47014 | 47014 | 47014 | 47014 |  | 47014 | 47014 | 47014 | °C | s16 | 10 | 50 | 700 | 200 | R/W
47015 | Min Supply System 1 |  | 47015 | 47015 | 47015 | 47015 | 47015 | 47015 | 47015 | 47015 | 47015 | 47015 | 47015 | 47015 | °C | s16 | 10 | 50 | 700 | 200 | R/W
47016 | Max Supply System 4 |  | 47016 | 47016 | 47016 | 47016 | 47016 | 47016 | 47016 | 47016 |  | 47016 | 47016 | 47016 | °C | s16 | 10 | 50 | 800 | 600 | R/W
47017 | Max Supply System 3 |  | 47017 | 47017 | 47017 | 47017 | 47017 | 47017 | 47017 | 47017 |  | 47017 | 47017 | 47017 | °C | s16 | 10 | 50 | 800 | 600 | R/W
47018 | Max Supply System 2 |  | 47018 | 47018 | 47018 | 47018 | 47018 | 47018 | 47018 | 47018 |  | 47018 | 47018 | 47018 | °C | s16 | 10 | 50 | 800 | 600 | R/W
47019 | Max Supply System 1 |  | 47019 | 47019 | 47019 | 47019 | 47019 | 47019 | 47019 | 47019 | 47019 | 47019 | 47019 | 47019 | °C | s16 | 10 | 50 | 800 | 600 | R/W
47020 | Own Heating Curve P7 | User defined heating curve point | 47020 | 47020 | 47020 | 47020 | 47020 | 47020 | 47020 | 47020 |  | 47020 | 47020 | 47020 | °C | s8 | 1 | 5 | 80 | 15 | R/W
47021 | Own Heating Curve P6 | User defined heating curve point | 47021 | 47021 | 47021 | 47021 | 47021 | 47021 | 47021 | 47021 |  | 47021 | 47021 | 47021 | °C | s8 | 1 | 5 | 80 | 15 | R/W
47022 | Own Heating Curve P5 | User defined heating curve point | 47022 | 47022 | 47022 | 47022 | 47022 | 47022 | 47022 | 47022 |  | 47022 | 47022 | 47022 | °C | s8 | 1 | 5 | 80 | 26 | R/W
47023 | Own Heating Curve P4 | User defined heating curve point | 47023 | 47023 | 47023 | 47023 | 47023 | 47023 | 47023 | 47023 |  | 47023 | 47023 | 47023 | °C | s8 | 1 | 5 | 80 | 32 | R/W
47024 | Own Heating Curve P3 | User defined heating curve point | 47024 | 47024 | 47024 | 47024 | 47024 | 47024 | 47024 | 47024 |  | 47024 | 47024 | 47024 | °C | s8 | 1 | 5 | 80 | 35 | R/W
47025 | Own Heating Curve P2 | User defined heating curve point | 47025 | 47025 | 47025 | 47025 | 47025 | 47025 | 47025 | 47025 |  | 47025 | 47025 | 47025 | °C | s8 | 1 | 5 | 80 | 40 | R/W
47026 | Own Heating Curve P1 | User defined heating curve point | 47026 | 47026 | 47026 | 47026 | 47026 | 47026 | 47026 | 47026 | 47026 | 47026 | 47026 | 47026 | °C | s8 | 1 | 5 | 80 | 45 | R/W
47027 | Point offset outdoor temp. | Outdoor temperature point where the heat curve is offset | 47027 | 47027 | 47027 | 47027 | 47027 | 47027 | 47027 | 47027 | 47027 | 47027 | 47027 | 47027 | °C | s8 | 1 | -40 | 30 | 0 | R/W
47028 | Point offset | Amount of offset at the point offset temperature | 47028 | 47028 | 47028 | 47028 | 47028 | 47028 | 47028 | 47028 | 47028 | 47028 | 47028 | 47028 | °C | s8 | 1 | -10 | 10 | 0 | R/W
47029 | External adjustment S4 | Change of the offset of the heat curve when closing the external adjustment input | 47029 | 47029 | 47029 | 47029 | 47029 | 47029 | 47029 | 47029 |  | 47029 | 47029 | 47029 |  | s8 | 1 | -10 | 10 | 0 | R/W
47030 | External adjustment S3 | Change of the offset of the heat curve when closing the external adjustment input | 47030 | 47030 | 47030 | 47030 | 47030 | 47030 | 47030 | 47030 |  | 47030 | 47030 | 47030 |  | s8 | 1 | -10 | 10 | 0 | R/W
47031 | External adjustment S2 | Change of the offset of the heat curve when closing the external adjustment input | 47031 | 47031 | 47031 | 47031 | 47031 | 47031 | 47031 | 47031 |  | 47031 | 47031 | 47031 |  | s8 | 1 | -10 | 10 | 0 | R/W
47032 | External adjustment S1 | Change of the offset of the heat curve when closing the external adjustment input | 47032 | 47032 | 47032 | 47032 | 47032 | 47032 | 47032 | 47032 | 47032 | 47032 | 47032 | 47032 |  | s8 | 1 | -10 | 10 | 0 | R/W
47033 | External adjustment with room sensor S4 | Room temperature setting when closing the external adjustment input | 47033 | 47033 | 47033 | 47033 | 47033 | 47033 | 47033 | 47033 |  | 47033 | 47033 | 47033 | °C | s16 | 10 | 50 | 300 | 200 | R/W
47034 | External adjustment with room sensor S3 | Room temperature setting when closing the external adjustment input | 47034 | 47034 | 47034 | 47034 | 47034 | 47034 | 47034 | 47034 |  | 47034 | 47034 | 47034 | °C | s16 | 10 | 50 | 300 | 200 | R/W
47035 | External adjustment with room sensor S2 | Room temperature setting when closing the external adjustment input | 47035 | 47035 | 47035 | 47035 | 47035 | 47035 | 47035 | 47035 |  | 47035 | 47035 | 47035 | °C | s16 | 10 | 50 | 300 | 200 | R/W
47036 | External adjustment with room sensor S1 | Room temperature setting when closing the external adjustment input | 47036 | 47036 | 47036 | 47036 | 47036 | 47036 | 47036 | 47036 | 47036 | 47036 | 47036 | 47036 | °C | s16 | 10 | 50 | 300 | 200 | R/W
47041 | Hot water comfort mode | Setting in menu 2.2. 0=Economy,1=Normal,2=Luxury,4=Smart Control 0=Economy 1=Normal 2=Luxury | 47041 | 47041 | 47041 | 47041 | 47041 | 47041 | 47041 | 47041 | 47041 | 47041 | 47041 | 47041 |  | s8 | 1 | 0 | 4 | 1 | R/W
47043 | Start temperature HW Luxury | Start temperature for heating water | 47043 | 47043 | 47043 | 47043 | 47043 | 47043 | 47043 | 47043 | 47043 | 47043 | 47043 | 47043 | °C | s16 | 10 | 50 | 700 | 520 | R/W
47044 | Start temperature HW Normal | Start temperature for heating water | 47044 | 47044 | 47044 | 47044 | 47044 | 47044 | 47044 | 47044 | 47044 | 47044 | 47044 | 47044 | °C | s16 | 10 | 50 | 700 | 490 | R/W
47045 | Start temperature HW Economy | Start temperature for heating water | 47045 | 47045 | 47045 | 47045 | 47045 | 47045 | 47045 | 47045 | 47045 | 47045 | 47045 | 47045 | °C | s16 | 10 | 50 | 700 | 450 | R/W
47046 | Stop temperature Periodic HW | Temperature where hot water generation will stop | 47046 | 47046 | 47046 | 47046 | 47046 | 47046 | 47046 | 47046 | 47046 | 47046 | 47046 | 47046 | °C | s16 | 10 | 550 | 700 | 550 | R/W
47047 | Stop temperature HW Luxury | Temperature where hot water generation will stop | 47047 | 47047 | 47047 | 47047 | 47047 | 47047 | 47047 | 47047 | 47047 | 47047 | 47047 | 47047 | °C | s16 | 10 | 50 | 700 | 580 | R/W
47048 | Stop temperature HW Normal | Temperature where hot water generation will stop | 47048 | 47048 | 47048 | 47048 | 47048 | 47048 | 47048 | 47048 | 47048 | 47048 | 47048 | 47048 | °C | s16 | 10 | 50 | 700 | 550 | R/W
47049 | Stop temperature HW Economy | Temperature where hot water generation will stop | 47049 | 47049 | 47049 | 47049 | 47049 | 47049 | 47049 | 47049 | 47049 | 47049 | 47049 | 47049 | °C | s16 | 10 | 50 | 700 | 510 | R/W
47050 | Periodic HW | Activates the periodic hot water generation | 47050 | 47050 | 47050 | 47050 | 47050 | 47050 | 47050 | 47050 | 47050 | 47050 | 47050 |  |  | s8 | 1 | 0 | 1 | 1 | R/W
47051 | Periodic HW Interval | Interval between Periodic hot water sessions | 47051 | 47051 | 47051 | 47051 | 47051 | 47051 | 47051 | 47051 | 47051 | 47051 | 47051 |  | days | s8 | 1 | 1 | 90 | 14 | R/W
47054 | Run time HWC | Run time for the hot water circulation system | 47054 | 47054 | 47054 | 47054 | 47054 | 47054 | 47054 | 47054 | 47054 | 47054 | 47054 | 47054 | min | s8 | 1 | 1 | 60 | 60 | R/W
47055 | Still time HWC | Still time for the hot water circulation system | 47055 | 47055 | 47055 | 47055 | 47055 | 47055 | 47055 | 47055 | 47055 | 47055 | 47055 | 47055 | min | s8 | 1 | 0 | 60 | 0 | R/W
47062 | HW charge offset | Offset of HW charge temperature from the stop temperature |  |  | 47062 | [9 empty] | °C | s8 | 10 | 0 | 0 | 0 | R/W
47092 | Manual compfreq HW | Should the compressor frequency be manual set in HW? |  |  | 47092 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R/W
47093 | Manual compfreq speed HW | Manual compressor frequency in HW? |  |  | 47093 | [9 empty] | Hz | u16 | 1 | 0 | 0 | 0 | R/W
47094 | Sec per compfreq step | Time between changes of the copmpressor frequency |  |  | 47094 | [9 empty] | s | u8 | 1 | 0 | 0 | 0 | R/W
47095 | Max compfreq step | Largest allowed change of compressor frequency in normal run |  |  | 47095 | [9 empty] | Hz | u8 | 1 | 0 | 0 | 0 | R/W
47096 | Manual compfreq Heating | Should the compressor frequency be manual set in Heating? |  |  | 47096 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R/W
47097 | Min speed after start | Time with minimum compressor frequency when heating demand occurs |  |  | 47097 | [9 empty] | Min | u8 | 1 | 0 | 0 | 0 | R/W
47098 | Min speed after HW | Should the compressor frequency be manual set in HW? |  |  | 47098 | [9 empty] | Min | u8 | 1 | 0 | 0 | 0 | R/W
47099 | GMz | Compressor frequency regulator GMz |  |  | 47099 |  | 47099 | [8 empty] | u8 | 1 | 0 | 0 | 0 | R/W
47100 | Max diff VBF-BerVBF | Largest allowed difference between Supply and calc supply |  |  | 47100 | 47100 | 47100 |  | 47100 | [5 empty] | °C | u8 | 10 | 0 | 0 | 0 | R/W
47101 | Comp freq reg P | Compressor frequency regulator P |  |  | 47101 | 47101 | 47101 |  | 47101 | [6 empty] | u8 | 1 | 0 | 0 | 0 | R/W
47102 | Comp freq max delta F | Maximum change of copmpressor frequency in compressor frequency regulator |  |  | 47102 | 47102 | 47102 |  | 47102 | [5 empty] | Hz | s8 | 1 | 0 | 0 | 0 | R/W
47103 | Min comp freq | Minimum allowed compressor frequency |  |  | 47103 | 47103 | 47103 |  | 47103 | [5 empty] | Hz | s16 | 1 | 0 | 0 | 0 | R/W
47104 | Max comp freq | Maximum allowed compressor frequency |  |  | 47104 | 47104 | 47104 |  | 47104 | [5 empty] | Hz | s16 | 1 | 0 | 0 | 0 | R/W
47105 | Comp freq heating | Compressor frequency used in heating mode |  |  | 47105 | [9 empty] | Hz | s16 | 1 | 0 | 0 | 0 | R/W
47131 | Language | Display language in the heat pump 0=English 1=Svenska 2=Deutsch 3=Francais 4=Espanol 5=Suomi 6=Lietuviu 7=Cesky 8=Polski 9=Nederlands 10=Norsk 11=Dansk 12=Eesti 13=Latviesu 16=Magyar | 47131 | 47131 | 47131 | 47131 | 47131 | 47131 | 47131 | 47131 | 47131 | 47131 | 47131 | 47131 |  | s8 | 1 | 0 | 21 | 0 | R/W
47134 | Period HW |  |  |  | 47134 | 47134 | 47134 | 47134 | 47134 | 47134 | 47134 | 47134 | 47134 | 47134 | min | u8 | 1 | 0 | 180 | 60 | R/W
47135 | Period Heat |  |  |  | 47135 | 47135 | 47135 | 47135 | 47135 | 47135 | 47135 | 47135 | 47135 | 47135 | min | u8 | 1 | 0 | 180 | 0 | R/W
47136 | Period Pool | [5 empty] | 47136 | 47136 | 47136 | 47136 |  | 47136 | 47136 | 47136 | min | u8 | 1 | 0 | 180 | 0 | R/W
47137 | Operational mode | The operational mode of the heat pump 0=Auto 1=Manual 2=Add. heat only | 47137 | 47137 | 47137 | 47137 | 47137 | 47137 | 47137 | 47137 | 47137 | 47137 | 47137 | 47137 |  | u8 | 1 | 0 | 2 | 0 | R/W
47138 | Operational mode heat medium pump | 10=Intermittent 20=Continous 30=Economy 40=Auto | 47138 | 47138 | 47138 | 47138 | 47138 | 47138 | 47138 | 47138 | 47138 | 47138 | 47138 | 47138 |  | u8 | 1 | 10 | 40 | 40 | R/W
47139 | Operational mode brine medium pump | 10=Intermittent 20=Continuous 30=Economy 40=Auto |  |  |  |  | 47139 | 47139 | 47139 | 47139 | [5 empty] | u8 | 1 | 10 | 30 | 10 | R/W
47206 | DM start heating | The value the degree minutes needed to be reached for the pump to start heating |  |  | 47206 | 47206 | 47206 | 47206 | 47206 | 47206 | 47206 | 47206 | 47206 | 47206 |  | s16 | 1 | -1000 | -30 | -60 | R/W
47209 | DM between add. steps | The number of degree minutes between start of each electric addition step |  |  | 47209 | 47209 | 47209 | 47209 | 47209 | 47209 | 47209 | 47209 | 47209 | 47209 |  | s16 | 1 | 0 | 0 | 0 | R/W
47210 | DM start add. with shunt |  |  |  | 47210 |  | 47210 | 47210 | 47210 | 47210 |  | 47210 | 47210 |  |  | s16 | 1 | -2000 | -30 | -400 | R/W
47212 | Max int add. power |  | 47212 | 47212 | 47212 | 47212 | 47212 | 47212 |  |  |  |  | 47212 | 47212 | kW | s16 | 100 | 0 | 4500 | 600 | R/W
47214 | Fuse | Size of the fuse that the HP is connected to | 47214 | 47214 | 47214 | 47214 | 47214 | 47214 | 47214 | 47214 | 47214 | 47214 | 47214 | 47214 | A | u16 | 1 | 1 | 400 | 16 | R/W
47261 | Exhaust Fan speed 4 |  | 47261 | 47261 | 47261 | 47261 | 47261 | 47261 | 47261 | 47261 |  |  |  |  | % | u8 | 1 | 0 | 100 | 100 | R/W
47262 | Exhaust Fan speed 3 |  | 47262 | 47262 | 47262 | 47262 | 47262 | 47262 | 47262 | 47262 |  |  |  |  | % | u8 | 1 | 0 | 100 | 80 | R/W
47263 | Exhaust Fan speed 2 |  | 47263 | 47263 | 47263 | 47263 | 47263 | 47263 | 47263 | 47263 |  |  |  |  | % | u8 | 1 | 0 | 100 | 30 | R/W
47264 | Exhaust Fan speed 1 |  | 47264 | 47264 | 47264 | 47264 | 47264 | 47264 | 47264 | 47264 |  |  |  |  | % | u8 | 1 | 0 | 100 | 0 | R/W
47265 | Exhaust Fan speed normal |  | 47265 | 47265 | 47265 | 47265 | 47265 | 47265 | 47265 | 47265 |  |  |  |  | % | u8 | 1 | 0 | 100 | 65 | R/W
47266 | Supply Fan speed 4 |  | 47266 | 47266 | 47266 | [9 empty] | % | u8 | 1 | 0 | 100 | 90 | R/W
47267 | Supply Fan speed 3 |  | 47267 | 47267 | 47267 | [9 empty] | % | u8 | 1 | 0 | 100 | 70 | R/W
47268 | Supply Fan speed 2 |  | 47268 | 47268 | 47268 | [9 empty] | % | u8 | 1 | 0 | 100 | 25 | R/W
47269 | Supply Fan speed 1 |  | 47269 | 47269 | 47269 | [9 empty] | % | u8 | 1 | 0 | 100 | 0 | R/W
47270 | Supply Fan speed normal |  | 47270 | 47270 | 47270 | [9 empty] | % | u8 | 1 | 0 | 100 | 60 | R/W
47271 | Fan return time 4 | Time from a changed fan speed until it returns to normal speed | 47271 | 47271 | 47271 | 47271 | 47271 | 47271 | 47271 | 47271 |  | 47271 | 47271 | 47271 | h | u8 | 1 | 1 | 99 | 4 | R/W
47272 | Fan return time 3 | Time from a changed fan speed until it returns to normal speed | 47272 | 47272 | 47272 | 47272 | 47272 | 47272 | 47272 | 47272 |  | 47272 | 47272 | 47272 | h | u8 | 1 | 1 | 99 | 4 | R/W
47273 | Fan return time 2 | Time from a changed fan speed until it returns to normal speed | 47273 | 47273 | 47273 | 47273 | 47273 | 47273 | 47273 | 47273 |  | 47273 | 47273 | 47273 | h | u8 | 1 | 1 | 99 | 4 | R/W
47274 | Fan return time 1 | Time from a changed fan speed until it returns to normal speed | 47274 | 47274 | 47274 | 47274 | 47274 | 47274 | 47274 | 47274 |  | 47274 | 47274 | 47274 | h | u8 | 1 | 1 | 99 | 4 | R/W
47275 | Filter Reminder period | Time between the reminder of filter replacement/cleaning. | 47275 | 47275 | 47275 | 47275 | 47275 | 47275 | 47275 | 47275 |  | 47275 | 47275 | 47275 | Months | u8 | 1 | 1 | 24 | 3 | R/W
47276 | Floor drying | 0=Off 1=On | 47276 | 47276 | 47276 | 47276 | 47276 | 47276 | 47276 | 47276 | 47276 | 47276 | 47276 | 47276 |  | u8 | 1 | 0 | 1 | 0 | R/W
47277 | Floor drying period 7 | Days each period is active | 47277 | 47277 | 47277 | 47277 | 47277 | 47277 | 47277 | 47277 | 47277 | 47277 | 47277 | 47277 | days | u8 | 1 | 0 | 30 | 2 | R/W
47278 | Floor drying period 6 | Days each period is active | 47278 | 47278 | 47278 | 47278 | 47278 | 47278 | 47278 | 47278 | 47278 | 47278 | 47278 | 47278 | days | u8 | 1 | 0 | 30 | 2 | R/W
47279 | Floor drying period 5 | Days each period is active | 47279 | 47279 | 47279 | 47279 | 47279 | 47279 | 47279 | 47279 | 47279 | 47279 | 47279 | 47279 | days | u8 | 1 | 0 | 30 | 2 | R/W
47280 | Floor drying period 4 | Days each period is active | 47280 | 47280 | 47280 | 47280 | 47280 | 47280 | 47280 | 47280 | 47280 | 47280 | 47280 | 47280 | days | u8 | 1 | 0 | 30 | 3 | R/W
47281 | Floor drying period 3 | Days each period is active | 47281 | 47281 | 47281 | 47281 | 47281 | 47281 | 47281 | 47281 | 47281 | 47281 | 47281 | 47281 | days | u8 | 1 | 0 | 30 | 2 | R/W
47282 | Floor drying period 2 | Days each period is active | 47282 | 47282 | 47282 | 47282 | 47282 | 47282 | 47282 | 47282 | 47282 | 47282 | 47282 | 47282 | days | u8 | 1 | 0 | 30 | 2 | R/W
47283 | Floor drying period 1 | Days each period is active | 47283 | 47283 | 47283 | 47283 | 47283 | 47283 | 47283 | 47283 | 47283 | 47283 | 47283 | 47283 | days | u8 | 1 | 0 | 30 | 2 | R/W
47284 | Floor drying temp. 7 | Supply temperature each period | 47284 | 47284 | 47284 | 47284 | 47284 | 47284 | 47284 | 47284 | 47284 | 47284 | 47284 | 47284 | °C | u8 | 1 | 15 | 70 | 20 | R/W
47285 | Floor drying temp. 6 | Supply temperature each period | 47285 | 47285 | 47285 | 47285 | 47285 | 47285 | 47285 | 47285 | 47285 | 47285 | 47285 | 47285 | °C | u8 | 1 | 15 | 70 | 30 | R/W
47286 | Floor drying temp. 5 | Supply temperature each period | 47286 | 47286 | 47286 | 47286 | 47286 | 47286 | 47286 | 47286 | 47286 | 47286 | 47286 | 47286 | °C | u8 | 1 | 15 | 70 | 40 | R/W
47287 | Floor drying temp. 4 | Supply temperature each period | 47287 | 47287 | 47287 | 47287 | 47287 | 47287 | 47287 | 47287 | 47287 | 47287 | 47287 | 47287 | °C | u8 | 1 | 15 | 70 | 45 | R/W
47288 | Floor drying temp. 3 | Supply temperature each period | 47288 | 47288 | 47288 | 47288 | 47288 | 47288 | 47288 | 47288 | 47288 | 47288 | 47288 | 47288 | °C | u8 | 1 | 15 | 70 | 40 | R/W
47289 | Floor drying temp. 2 | Supply temperature each period | 47289 | 47289 | 47289 | 47289 | 47289 | 47289 | 47289 | 47289 | 47289 | 47289 | 47289 | 47289 | °C | u8 | 1 | 15 | 70 | 30 | R/W
47290 | Floor drying temp. 1 | Supply temperature each period | 47290 | 47290 | 47290 | 47290 | 47290 | 47290 | 47290 | 47290 | 47290 | 47290 | 47290 | 47290 | °C | u8 | 1 | 15 | 70 | 20 | R/W
47291 | Floor drying timer |  | 47291 | 47291 | 47291 | 47291 | 47291 | 47291 | 47291 | 47291 | 47291 | 47291 | 47291 | 47291 | hrs | u16 | 1 | 0 | 10000 | 0 | R
47292 | Trend temperature | Above the set outdoor temperature the addition activation time is limited to give the compressor more time to raise the hot water temperature. | 47292 | 47292 | [10 empty] | °C | s16 | 10 | 0 | 200 | 70 | R/W
47293 | Transfer time HW-Heat | Time between hot water and heating operating mode | 47293 | 47293 | [10 empty] | mins | s8 | 1 | 1 | 60 | 45 | R/W
47294 | Use airflow defrost | If reduced airflow should start defrost |  |  | 47294 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R/W
47295 | Airflow reduction trig | How much the airflow is allowed to be reduced before a defrost is trigged |  |  | 47295 | [9 empty] | % | u8 | 1 | 0 | 0 | 0 | R/W
47296 | Airflow defrost done | How much the airflow has to raise before a defrost is ended |  |  | 47296 | [9 empty] | % | u8 | 1 | 0 | 0 | 0 | R/W
47299 | Min time defrost | Minimum duration of the defrost |  |  | 47299 | [9 empty] | min | u8 | 1 | 0 | 0 | 0 | R/W
47300 | DOT | Dimensioning outdoor temperature | 47300 | 47300 | 47300 | 47300 | 47300 | 47300 | 47300 | 47300 | 47300 | 47300 | 47300 | 47300 | °C | s16 | 10 | -400 | 200 | -180 | R/W
47301 | delta T at DOT | Delta T (BT12-BT3)at dimensioning outdoor temperature | 47301 | 47301 | 47301 | 47301 | 47301 | 47301 | 47301 | 47301 | 47301 | 47301 | 47301 | 47301 | °C | s16 | 10 | 10 | 250 | 100 | R/W
47302 | Climate system 2 accessory | Activates the climate system 2 accessory 0=Off 1=On | 47302 | 47302 | 47302 | 47302 | 47302 | 47302 | 47302 | 47302 |  | 47302 | 47302 | 47302 |  | u8 | 1 | 0 | 1 | 0 | R/W
47303 | Climate system 3 accessory | Activates the climate system 3 accessory 0=Off 1=On | 47303 | 47303 | 47303 | 47303 | 47303 | 47303 | 47303 | 47303 |  | 47303 | 47303 | 47303 |  | u8 | 1 | 0 | 1 | 0 | R/W
47304 | Climate system 4 accessory | Activates the climate system 4 accessory 0=Off 1=On | 47304 | 47304 | 47304 | 47304 | 47304 | 47304 | 47304 | 47304 |  | 47304 | 47304 | 47304 |  | u8 | 1 | 0 | 1 | 0 | R/W
47305 | Climate system 4 mixing valve amp. | Mixing valve amplification for extra climate systems | 47305 | 47305 | 47305 | 47305 | 47305 | 47305 | 47305 | 47305 |  | 47305 | 47305 | 47305 |  | s8 | 10 | 1 | 100 | 10 | R/W
47306 | Climate system 3 mixing valve amp. | Mixing valve amplification for extra climate systems | 47306 | 47306 | 47306 | 47306 | 47306 | 47306 | 47306 | 47306 |  | 47306 | 47306 | 47306 |  | s8 | 10 | 1 | 100 | 10 | R/W
47307 | Climate system 2 mixing valve amp. | Mixing valve amplification for extra climate systems | 47307 | 47307 | 47307 | 47307 | 47307 | 47307 | 47307 | 47307 |  | 47307 | 47307 | 47307 |  | s8 | 10 | 1 | 100 | 10 | R/W
47308 | Climate system 4 shunt wait | Wait time between changes of the shunt in extra climate systems | 47308 | 47308 | 47308 | 47308 | 47308 | 47308 | 47308 | 47308 |  | 47308 | 47308 | 47308 | secs | s16 | 10 | 10 | 300 | 30 | R/W
47309 | Climate system 3 shunt wait | Wait time between changes of the shunt in extra climate systems | 47309 | 47309 | 47309 | 47309 | 47309 | 47309 | 47309 | 47309 |  | 47309 | 47309 | 47309 | secs | s16 | 10 | 10 | 300 | 30 | R/W
47310 | Climate system 2 shunt wait | Wait time between changes of the shunt in extra climate systems | 47310 | 47310 | 47310 | 47310 | 47310 | 47310 | 47310 | 47310 |  | 47310 | 47310 | 47310 | secs | s16 | 10 | 10 | 300 | 30 | R/W
47312 | FLM pump 1 | Operating mode for the FLM pump 1¦Operating mode for the FLM pump 2¦Operating mode for the FLM pump 3¦Operating mode for the FLM pump 4 0=Off 1=On |  |  |  |  | 47312 | 47312 | 47312 | 47312 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47313 | FLM 1 defrost | Minimum time between defrost in FLM 1¦Minimum time between defrost in FLM 2¦Minimum time between defrost in FLM 3¦Minimum time between defrost in FLM 4 |  |  |  |  | 47313 | 47313 | 47313 | 47313 |  |  |  |  | hrs | u8 | 1 | 1 | 30 | 10 | R/W
47317 | Shunt controlled add. accessory | Activates the shunt controlled addition accessory. 1=on,0=off 0=Off 1=On |  |  | 47317 |  | 47317 | 47317 | 47317 | 47317 |  | 47317 | 47317 | 47317 |  | u8 | 1 | 0 | 1 | 0 | R/W
47318 | Shunt controlled add. min. temp. |  |  |  | 47318 |  | 47318 | 47318 | 47318 | 47318 |  | 47318 | 47318 | 47318 | °C | s8 | 1 | 5 | 90 | 55 | R/W
47319 | Shunt controlled add. min. runtime |  |  |  | 47319 |  | 47319 | 47319 | 47319 | 47319 |  | 47319 | 47319 | 47319 | hrs | u8 | 1 | 0 | 48 | 12 | R/W
47320 | Shunt controlled add. mixing valve amp. | Mixing valve amplification for shunt controlled add. |  |  | 47320 |  | 47320 | 47320 | 47320 | 47320 |  | 47320 | 47320 | 47320 |  | s8 | 10 | 1 | 100 | 10 | R/W
47321 | Shunt controlled add. mixing valve wait | Wait time between changes of the shunt in shunt controlled add. |  |  | 47321 |  | 47321 | 47321 | 47321 | 47321 |  | 47321 | 47321 | 47321 | secs | s16 | 1 | 10 | 300 | 30 | R/W
47322 | Step controlled add. accessory | Activates the step controlled addition accessory 0=Off 1=On |  |  |  |  | 47322 | 47322 | 47322 | 47322 |  | 47322 | 47322 |  |  | u8 | 1 | 0 | 1 | 0 | R/W
47323 | Step controlled add. start DM | DM where the first step of step controlled add. starts | [8 empty] | 47323 |  | 47323 |  |  | s16 | 1 | -2000 | -30 | -400 | R/W
47324 | Step controlled add. diff. DM | Difference in DM of each step in the step controlled add. |  |  |  |  | 47324 | 47324 | 47324 | 47324 | 47324 | 47324 | 47324 | 47324 |  | s16 | 1 | 0 | 1000 | 100 | R/W
47325 | Step controlled add. max. step | Maximum number of steps allowed in step controlled add. |  |  |  |  | 47325 | 47325 | 47325 | 47325 | 47325 | 47325 | 47325 | 47325 |  | u8 | 1 | 0 | 7 | 3 | R
47326 | Step controlled add. mode | Binary or linear stepping method. 0=Linear 1=Binary |  |  |  |  | 47326 | 47326 | 47326 | 47326 | 47326 | 47326 | 47326 | 47326 |  | u8 | 1 | 0 | 1 | 0 | R/W
47327 | Ground water pump accessory | Ground water pump using AXC40 0=Off 1=On |  |  |  |  | 47327 | 47327 | 47327 | 47327 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47329 | Cooling 2-pipe accessory | Activates the 2-pipe cooling accessory 0=Off 1=On |  |  |  |  | 47329 | 47329 | 47329 | 47329 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47330 | Cooling 4-pipe accessory | Activates the 4-pipe cooling accessory 0=Off 1=On |  |  |  |  | 47330 | 47330 | 47330 | 47330 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47335 | Time betw. switch heat/cool | Time between switching from heating to cooling or vice versa. |  |  |  |  | 47335 | 47335 | 47335 | 47335 | 47335 | 47335 | 47335 | 47335 | h | s8 | 1 | 0 | 48 | 2 | R/W
47336 | Heat at room under temp. | This value indicates how many degrees under set room temp heating will be allowed |  |  |  |  | 47336 | 47336 | 47336 | 47336 | 47336 | 47336 | 47336 | 47336 | °C | s8 | 10 | 5 | 100 | 10 | R/W
47337 | Cool at room over temp. | This value indicates how many degrees over set room temp cooling will be allowed |  |  |  |  | 47337 | 47337 | 47337 | 47337 | 47337 | 47337 | 47337 | 47337 | °C | s8 | 10 | 5 | 100 | 30 | R/W
47338 | Cooling mix. valve amp. | Mixing valve amplification for the cooling valve |  |  |  |  | 47338 | 47338 | 47338 | 47338 | [5 empty] | s8 | 10 | 1 | 100 | 10 | R/W
47339 | Cooling mix. valve step delay | [5 empty] | 47339 | 47339 | 47339 | 47339 |  | 47339 |  | 47339 | s | s16 | 1 | 10 | 300 | 30 | R/W
47340 | Cooling with room sensor | Enables use of room sensor together with cooling 0=Off 1=On |  |  |  |  | 47340 | 47340 | 47340 | 47340 | 47340 | 47340 | 47340 | 47340 |  | u8 | 10 | 0 | 18 | 0 | R/W
47341 | HPAC accessory | Activates the HPAC accessory |  |  |  |  | 47341 | 47341 | 47341 | 47341 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47342 | Start Passive Cooling DM | Value the degree minutes have to reach to start passive cooling |  |  |  |  | 47342 | 47342 | 47342 | 47342 | [5 empty] | s16 | 1 | 10 | 500 | 30 | R/W
47343 | Start Active Cooling DM | Value the degree minutes have to reach to start active cooling |  |  |  |  | 47343 | 47343 | 47343 | 47343 | 47343 | 47343 | 47343 | 47343 |  | s16 | 1 | 10 | 300 | 90 | R/W
47351 | FJVM accessory | Activates the FJVM accessory 0=Off 1=On | 47351 | 47351 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47352 | SMS40 accessory | Activates the SMS40 accessory | 47352 | 47352 | 47352 | 47352 | 47352 | 47352 | 47352 | 47352 |  | 47352 | 47352 | 47352 |  | u8 | 1 | 0 | 1 | 0 | R/W
47365 | RMU System 1 | Activates the RMU accessory for system 1 | 47365 | 47365 | 47365 |  | 47365 | 47365 | 47365 | 47365 |  | 47365 | 47365 | 47365 |  | u8 | 1 | 0 | 1 | 0 | R/W
47366 | RMU System 2 | Activates the RMU accessory for system 2 | 47366 | 47366 | 47366 |  | 47366 | 47366 | 47366 | 47366 |  | 47366 | 47366 | 47366 |  | u8 | 1 | 0 | 1 | 0 | R/W
47367 | RMU System 3 | Activates the RMU accessory for system 3 | 47367 | 47367 | 47367 |  | 47367 | 47367 | 47367 | 47367 |  | 47367 | 47367 | 47367 |  | u8 | 1 | 0 | 1 | 0 | R/W
47368 | RMU System 4 | Activates the RMU accessory for system 4 | 47368 | 47368 | 47368 |  | 47368 | 47368 | 47368 | 47368 |  | 47368 | 47368 | 47368 |  | u8 | 1 | 0 | 1 | 0 | R/W
47370 | Allow Additive Heating | Whether to allow additive heating (only valid for operational mode Manual) | 47370 | 47370 | 47370 | 47370 | 47370 | 47370 | 47370 | 47370 | 47370 | 47370 | 47370 | 47370 |  | u8 | 1 | 0 | 1 | 1 | R/W
47371 | Allow Heating | Whether to allow heating (only valid for operational mode Manual or Add. heat only) | 47371 | 47371 | 47371 | 47371 | 47371 | 47371 | 47371 | 47371 | 47371 | 47371 | 47371 | 47371 |  | u8 | 1 | 0 | 1 | 1 | R/W
47372 | Allow Cooling | Whether to allow cooling (only valid for operational mode Manual or Add. heat only) | 47372 | 47372 |  |  | 47372 | 47372 | 47372 | 47372 | 47372 | 47372 | 47372 | 47372 |  | u8 | 1 | 0 | 1 | 1 | R/W
47374 | Start Temperature Cooling | Start temperature for cooling, as set in menu 4.9.2 0=Off 1=On | 47374 | 47374 | 47374 | 47374 | 47374 | 47374 | 47374 | 47374 | 47374 | 47374 | 47374 | 47374 | °C | s16 | 10 | -200 | 400 | 250 | R/W
47375 | Stop Temperature Heating | Stop temperature for heating, as set in menu 4.9.2 | 47375 | 47375 | 47375 | 47375 | 47375 | 47375 | 47375 | 47375 | 47375 | 47375 | 47375 | 47375 | °C | s16 | 10 | -200 | 400 | 170 | R/W
47376 | Stop Temperature Additive | Stop temperature for additive, as set in menu 4.9.2 | 47376 | 47376 | 47376 | 47376 | 47376 | 47376 | 47376 | 47376 | 47376 | 47376 | 47376 | 47376 | °C | s16 | 10 | -250 | 400 | 150 | R/W
47377 | Outdoor Filter Time | 12=12 Hours 24=24 Hours | 47377 | 47377 | 47377 | 47377 | 47377 | 47377 | 47377 | 47377 | 47377 | 47377 | 47377 | 47377 | h | u8 | 1 | 0 | 48 | 24 | R/W
47378 | Max diff. comp. |  | 47378 | 47378 | 47378 | 47378 | 47378 | 47378 | 47378 | 47378 | 47378 | 47378 | 47378 | 47378 | °C | s16 | 10 | 10 | 250 | 100 | R/W
47379 | Max diff. add. |  | 47379 | 47379 | 47379 | 47379 | 47379 | 47379 | 47379 | 47379 | 47379 | 47379 | 47379 | 47379 | °C | s16 | 10 | 10 | 240 | 70 | R/W
47380 | Low brine out autoreset | 0=Off 1=On |  |  |  |  | 47380 | 47380 | 47380 | 47380 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47381 | Low brine out temp.EP14 | [5 empty] | 47381 | 47381 | 47381 | 47381 |  |  |  |  | °C | s16 | 10 | -120 | 150 | -80 | R/W
47382 | High brine in | Activates the High brine in temperature alarm. 0=Off 1=On |  |  |  |  | 47382 | 47382 | 47382 | 47382 | [5 empty] | u8 | 1 | 1 | 1 | 1 | R/W
47383 | High brine in temp. | The brine in temperature that triggers the high brine in temperature alarm (if active). |  |  |  |  | 47383 | 47383 | 47383 | 47383 |  |  |  |  | °C | s16 | 10 | 100 | 300 | 300 | R/W
47384 | Date format | 1=DD-MM-YY 2=YY-MM-DD | 47384 | 47384 | 47384 | 47384 | 47384 | 47384 | 47384 | 47384 | 47384 | 47384 | 47384 | 47384 |  | u8 | 1 | 1 | 2 | 1 | R/W
47385 | Time format | 12=12 hours 24=24 Hours | 47385 | 47385 | 47385 | 47385 | 47385 | 47385 | 47385 | 47385 | 47385 | 47385 | 47385 | 47385 |  | u8 | 1 | 12 | 24 | 24 | R/W
47387 | HW production | Activates hot water production where applicable 0=Off 1=On | 47387 | 47387 | 47387 | 47387 | 47387 | 47387 | 47387 | 47387 | 47387 | 47387 | 47387 | 47387 |  | u8 | 1 | 0 | 1 | 0 | R/W
47388 | Alarm lower room temp. | Lowers the room temperature during red light alarms to notify the occupants of the building that something is the matter 0=Off 1=On | 47388 | 47388 | 47388 | 47388 | 47388 | 47388 | 47388 | 47388 | 47388 | 47388 | 47388 | 47388 |  | u8 | 1 | 0 | 1 | 0 | R/W
47389 | Alarm lower HW temp. | Lowers the hot water temperature during red light alarms to notify the occupants of the building that something is the matter 0=Off 1=On | 47389 | 47389 | 47389 | 47389 | 47389 | 47389 | 47389 | 47389 | 47389 | 47389 | 47389 | 47389 |  | u8 | 1 | 0 | 1 | 1 | R/W
47391 | Use room sensor S4 | When activated the system uses the room sensor 0=Off 1=On | 47391 | 47391 | 47391 | 47391 | 47391 | 47391 | 47391 | 47391 |  | 47391 | 47391 | 47391 |  | u8 | 1 | 0 | 1 | 0 | R/W
47392 | Use room sensor S3 | When activated the system uses the room sensor 0=Off 1=On | 47392 | 47392 | 47392 | 47392 | 47392 | 47392 | 47392 | 47392 |  | 47392 | 47392 | 47392 |  | u8 | 1 | 0 | 1 | 0 | R/W
47393 | Use room sensor S2 | When activated the system uses the room sensor 0=Off 1=On | 47393 | 47393 | 47393 | 47393 | 47393 | 47393 | 47393 | 47393 |  | 47393 | 47393 | 47393 |  | u8 | 1 | 0 | 1 | 0 | R/W
47394 | Use room sensor S1 | When activated the system uses the room sensor 0=Off 1=On | 47394 | 47394 | 47394 | 47394 | 47394 | 47394 | 47394 | 47394 | 47394 | 47394 | 47394 | 47394 |  | u8 | 1 | 0 | 1 | 0 | R/W
47395 | Room sensor setpoint S4 | Sets the room temperature setpoint for the system | 47395 | 47395 | 47395 | 47395 | 47395 | 47395 | 47395 | 47395 |  | 47395 | 47395 | 47395 | °C | s16 | 10 | 50 | 300 | 200 | R/W
47396 | Room sensor setpoint S3 | Sets the room temperature setpoint for the system | 47396 | 47396 | 47396 | 47396 | 47396 | 47396 | 47396 | 47396 |  | 47396 | 47396 | 47396 | °C | s16 | 10 | 50 | 300 | 200 | R/W
47397 | Room sensor setpoint S2 | Sets the room temperature setpoint for the system | 47397 | 47397 | 47397 | 47397 | 47397 | 47397 | 47397 | 47397 |  | 47397 | 47397 | 47397 | °C | s16 | 10 | 50 | 300 | 200 | R/W
47398 | Room sensor setpoint S1 | Sets the room temperature setpoint for the system | 47398 | 47398 | 47398 | 47398 | 47398 | 47398 | 47398 | 47398 | 47398 | 47398 | 47398 | 47398 | °C | s16 | 10 | 50 | 300 | 200 | R/W
47399 | Room sensor factor S4 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47399 | 47399 | 47399 | 47399 | 47399 | 47399 | 47399 | 47399 |  | 47399 | 47399 | 47399 |  | u8 | 10 | 0 | 60 | 10 | R/W
47400 | Room sensor factor S3 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47400 | 47400 | 47400 | 47400 | 47400 | 47400 | 47400 | 47400 |  | 47400 | 47400 | 47400 |  | u8 | 10 | 0 | 60 | 10 | R/W
47401 | Room sensor factor S2 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47401 | 47401 | 47401 | 47401 | 47401 | 47401 | 47401 | 47401 |  | 47401 | 47401 | 47401 |  | u8 | 10 | 0 | 60 | 10 | R/W
47402 | Room sensor factor S1 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47402 | 47402 | 47402 | 47402 | 47402 | 47402 | 47402 | 47402 | 47402 | 47402 | 47402 | 47402 |  | u8 | 10 | 0 | 60 | 10 | R/W
47413 | Speed circ.pump HW | [5 empty] | 47413 | 47413 | 47413 | 47413 |  |  |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
47414 | Speed circ.pump Heat | [5 empty] | 47414 | 47414 | 47414 | 47414 |  |  |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
47415 | Speed circ.pump Pool | [5 empty] | 47415 | 47415 | 47415 | 47415 |  |  |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
47416 | Speed circ.pump Economy | [5 empty] | 47416 | 47416 | 47416 | 47416 |  |  |  |  | % | u8 | 1 | 1 | 100 | 30 | R/W
47417 | Speed Circulation Pump Passive Cooling EP14 | [5 empty] | 47417 | 47417 | 47417 | 47417 |  |  |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
47418 | Speed brine pump | [5 empty] | 47418 | 47418 | 47418 | 47418 |  |  |  |  | % | u8 | 1 | 1 | 100 | 100 | R/W
47442 | preset flow clim. sys. | Preset flow setting for climate system. 0 = manual setting, 1 = radiator, 2 = floor heating, 3 = radiator + floor heating. | 47442 | 47442 | 47442 | 47442 | 47442 | 47442 | 47442 | 47442 | 47442 | 47442 | 47442 | 47442 |  | u8 | 1 | 0 | 3 | 1 | R/W
47473 | Max time defrost | Maximum duration of the defrost |  |  | 47473 | [9 empty] | min | u8 | 1 | 0 | 0 | 0 | R/W
47525 | Heat Curve S8 | Heat curve, see manual for more information | 47525 | 47525 | 47525 | 47525 | 47525 | 47525 | 47525 | 47525 |  | 47525 | 47525 | 47525 |  | s8 | 1 | 0 | 15 | 9 | R/W
47536 | Fan synch mode | If the fan should have a lower speed when the compressor is not running 0=Off 1=On | 47536 | 47536 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47537 | Night cooling | If the fan should have a higher speed when there is a high room temp and a low outdoor temp. 0=Off 1=On | 47537 | 47537 | 47537 | 47537 | 47537 | 47537 | 47537 | 47537 |  | 47537 | 47537 | 47537 |  | u8 | 1 | 0 | 1 | 0 | R/W
47538 | Start room temp. night cooling |  | 47538 | 47538 | 47538 | 47538 | 47538 | 47538 | 47538 | 47538 |  | 47538 | 47538 | 47538 | °C | u8 | 1 | 20 | 30 | 25 | R/W
47539 | Night Cooling Min. diff. | Minimum difference between room temp and outdoor temp to start night cooling | 47539 | 47539 | 47539 | 47539 | 47539 | 47539 | 47539 | 47539 |  | 47539 | 47539 | 47539 | °C | u8 | 1 | 3 | 10 | 6 | R/W
47540 | Heat DM diff | Difference in DM between compressor starts in heating mode | [5 empty] | 47540 | 47540 | 47540 |  | 47540 |  |  |  | s16 | 1 | 10 | 2000 | 60 | R/W
47543 | Cooling DM diff | Difference in DM between compressor starts in cooling mode | [5 empty] | 47543 | 47543 | 47543 |  | 47543 |  |  |  | s16 | 1 | 10 | 150 | 30 | R/W
47555 | DEW accessory | Activates the DEW accessory |  |  | 47555 | [10 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47556 | DEH accessory | Activates the DEH accessory | 47556 | 47556 | [11 empty] | u8 | 1 | 0 | 1 | 0 | R/W
47564 | Allow Heating Sys1 | Whether to allow heating for system 1 (only valid for operational mode Manual or Add. heat only) | 47564 | 47564 | [11 empty] | u8 | 1 | 0 | 1 | 1 | R/W
47565 | Allow Heating Sys2 | Whether to allow heating for system 2 (only valid for operational mode Manual or Add. heat only) | 47565 | 47565 | [11 empty] | u8 | 1 | 0 | 1 | 1 | R/W
47567 | Heat Curve S7 | Heat curve, see manual for more information | 47567 | 47567 | 47567 | 47567 | 47567 | 47567 | 47567 | 47567 |  | 47567 | 47567 | 47567 |  | s8 | 1 | 0 | 15 | 9 | R/W
47613 | Max Internal Add | Maximum allowed steps for the internally connected addition. | [6 empty] | 47613 | 47613 | 47613 | 47613 |  |  |  | u8 | 1 | 0 | 7 | 3 | R/W
47614 | Int. connected add. mode | Binary or linear stepping method for the internally connected external addition. 0=Linear 1=Binary | [6 empty] | 47614 | 47614 | 47614 | 47614 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
47631 | External add step controlled | Puts the external addition i step mode | [11 empty] | 47631 |  | u8 | 1 | 0 | 1 | 0 | R/W
47632 | External add. min. runtime | Min. runtime, only relevant if not step mode | [11 empty] | 47632 | hrs | u8 | 1 | 0 | 48 | 12 | R/W
47633 | State ext. add. | Only relevant if not in step mode | [11 empty] | 47633 |  | u8 | 1 | 0 | 0 | 0 | R
48043 | Holiday - Activated | 0=inactive, 10=active | 48043 | 48043 | 48043 | 48043 | 48043 | 48043 | 48043 | 48043 | 48043 | 48043 | 48043 | 48043 |  | u8 | 1 | 0 | 10 | 0 | R/W
48053 | FLM 2 speed 4 | [5 empty] | 48053 | 48053 | 48053 | 48053 |  |  |  |  | % | u8 | 1 | 0 | 100 | 100 | R/W
48054 | FLM 2 speed 3 | [5 empty] | 48054 | 48054 | 48054 | 48054 |  |  |  |  | % | u8 | 1 | 0 | 100 | 80 | R/W
48055 | FLM 2 speed 2 | [5 empty] | 48055 | 48055 | 48055 | 48055 |  |  |  |  | % | u8 | 1 | 0 | 100 | 30 | R/W
48056 | FLM 2 speed 1 | [5 empty] | 48056 | 48056 | 48056 | 48056 |  |  |  |  | % | u8 | 1 | 0 | 100 | 0 | R/W
48057 | FLM 2 speed normal | [5 empty] | 48057 | 48057 | 48057 | 48057 |  |  |  |  | % | u8 | 1 | 0 | 100 | 65 | R/W
48058 | FLM 3 speed 4 | [5 empty] | 48058 | 48058 | 48058 | 48058 |  |  |  |  | % | u8 | 1 | 0 | 100 | 100 | R/W
48059 | FLM 3 speed 3 | [5 empty] | 48059 | 48059 | 48059 | 48059 |  |  |  |  | % | u8 | 1 | 0 | 100 | 80 | R/W
48060 | FLM 3 speed 2 | [5 empty] | 48060 | 48060 | 48060 | 48060 |  |  |  |  | % | u8 | 1 | 0 | 100 | 30 | R/W
48061 | FLM 3 speed 1 | [5 empty] | 48061 | 48061 | 48061 | 48061 |  |  |  |  | % | u8 | 1 | 0 | 100 | 0 | R/W
48062 | FLM 3 speed normal | [5 empty] | 48062 | 48062 | 48062 | 48062 |  |  |  |  | % | u8 | 1 | 0 | 100 | 65 | R/W
48063 | FLM 4 speed 4 | [5 empty] | 48063 | 48063 | 48063 | 48063 |  |  |  |  | % | u8 | 1 | 0 | 100 | 100 | R/W
48064 | FLM 4 speed 3 | [5 empty] | 48064 | 48064 | 48064 | 48064 |  |  |  |  | % | u8 | 1 | 0 | 100 | 80 | R/W
48065 | FLM 4 speed 2 | [5 empty] | 48065 | 48065 | 48065 | 48065 |  |  |  |  | % | u8 | 1 | 0 | 100 | 30 | R/W
48066 | FLM 4 speed 1 | [5 empty] | 48066 | 48066 | 48066 | 48066 |  |  |  |  | % | u8 | 1 | 0 | 100 | 0 | R/W
48067 | FLM 4 speed normal | [5 empty] | 48067 | 48067 | 48067 | 48067 |  |  |  |  | % | u8 | 1 | 0 | 100 | 65 | R/W
48068 | FLM 4 accessory | Activates the FLM 4 accessory |  |  |  |  | 48068 | 48068 | 48068 | 48068 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48069 | FLM 3 accessory | Activates the FLM 3 accessory |  |  |  |  | 48069 | 48069 | 48069 | 48069 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48070 | FLM 2 accessory | Activates the FLM 2 accessory |  |  |  |  | 48070 | 48070 | 48070 | 48070 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48071 | FLM 1 accessory | Activates the FLM 1 accessory |  |  |  |  | 48071 | 48071 | 48071 | 48071 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48072 | DM diff start add. | The value below the last compressor step the degree minutes needed to be reached for the pump to start electric addition |  |  | 48072 | 48072 | 48072 | 48072 | 48072 | 48072 | 48072 | 48072 | 48072 | 48072 |  | s16 | 1 | 10 | 2400 | 700 | R/W
48073 | FLM 1 cooling | FLM 1 cooling activated¦FLM 2 cooling activated¦FLM 3 cooling activated¦FLM 4 cooling activated |  |  |  |  | 48073 | 48073 | 48073 | 48073 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48074 | Cool/Heat Sensor Set Point | Set point for change between cooling and heating when using the cool/heat sensor |  |  |  |  | 48074 | 48074 | 48074 | 48074 | 48074 | 48074 | 48074 | 48074 |  | s16 | 10 | 50 | 400 | 210 | R/W
48083 | Solar Pool Heating Active | 1=Yes, 0=No | [11 empty] | 48083 |  | u8 | 1 | 0 | 0 | 0 | R
48085 | Heat medium pump manual speed | Heat medium pump speed if manual | [8 empty] | 48085 | 48085 |  | 48085 | % | s8 | 1 | 1 | 100 | 70 | R/W
48086 | Hot water tank type | 10=VPB 20=VPA | [7 empty] | 48086 | [5 empty] | u8 | 1 | 10 | 20 | 20 | R/W
48087 | Pool 2 accessory | Activate the pool 2 accessory |  |  |  |  | 48087 | 48087 | 48087 | 48087 |  | 48087 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48088 | Pool 1 accessory | Activates the pool 1 accessory |  |  |  |  | 48088 | 48088 | 48088 | 48088 |  | 48088 | 48088 | 48088 |  | u8 | 1 | 0 | 1 | 0 | R/W
48089 | Pool 2 start temp. | The Temperature below which the pool heating should start |  |  |  |  | 48089 | 48089 | 48089 | 48089 |  | 48089 |  |  | °C | s16 | 10 | 50 | 800 | 220 | R/W
48090 | Pool 1 start temp. | The Temperature below which the pool heating should start |  |  |  |  | 48090 | 48090 | 48090 | 48090 |  | 48090 | 48090 | 48090 | °C | s16 | 10 | 50 | 800 | 220 | R/W
48091 | Pool 2 stop temp. | The Temperature at which the pool heating will stop |  |  |  |  | 48091 | 48091 | 48091 | 48091 |  | 48091 |  |  | °C | s16 | 10 | 50 | 800 | 240 | R/W
48092 | Pool 1 stop temp. | The Temperature at which the pool heating will stop |  |  |  |  | 48092 | 48092 | 48092 | 48092 |  | 48092 | 48092 | 48092 | °C | s16 | 10 | 50 | 800 | 240 | R/W
48093 | Pool 2 Activated | Activates pool heating |  |  |  |  | 48093 | 48093 | 48093 | 48093 |  | 48093 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48094 | Pool 1 Activated | Activates pool heating |  |  |  |  | 48094 | 48094 | 48094 | 48094 |  | 48094 | 48094 | 48094 |  | u8 | 1 | 0 | 1 | 1 | R/W
48099 | External add. accessory | Activates the external addition accessory | [11 empty] | 48099 |  | u8 | 1 | 0 | 1 | 0 | R/W
48107 | Charge pump manual speed | Charge pump speed if manual | [11 empty] | 48107 | % | s8 | 1 | 1 | 100 | 70 | R/W
48120 | HW Comfort | Activates the HW Comfort Accessory. |  |  |  |  | 48120 | 48120 | 48120 | 48120 |  |  | 48120 |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48130 | Manual heat medium pump speed | Manual heat medium pump speed? | [8 empty] | 48130 | 48130 |  | 48130 | % | s8 | 1 | 0 | 1 | 0 | R/W
48131 | Manual charge pump speed | Manual charge pump speed? | [11 empty] | 48131 | % | s8 | 1 | 0 | 1 | 0 | R/W
48132 | Temporary Lux | 0=Off, 1=3h, 2=6h, 3=12h, 4=One time increase | 48132 | 48132 | 48132 | 48132 | 48132 | 48132 | 48132 | 48132 | 48132 | 48132 | 48132 | 48132 |  | s8 | 1 | 0 | 0 | 0 | R/W
48133 | Period Pool 2 | [5 empty] | 48133 | 48133 | 48133 | 48133 |  | 48133 |  |  | min | u8 | 1 | 0 | 180 | 30 | R/W
48139 | DM startdiff add. with shunt |  |  |  | 48139 |  | 48139 | 48139 | 48139 | 48139 |  | 48139 | 48139 |  |  | s16 | 1 | 0 | 2000 | 400 | R/W
48140 | Max pool 2 compr. | Maximum number of compressors that are simultaneously charging the pool | [6 empty] | 48140 | 48140 |  | 48140 |  |  |  | u8 | 1 | 1 | 18 | 18 | R/W
48141 | Max pool 1 compr. | Maximum number of compressors that are simultaneously charging the pool | [6 empty] | 48141 | 48141 |  | 48141 |  |  |  | u8 | 1 | 1 | 18 | 18 | R/W
48142 | Step controlled add. start diff DM | DM diff from last compressor step where the first step of step controlled add. starts |  |  |  |  | 48142 | 48142 | 48142 | 48142 |  | 48142 |  |  |  | s16 | 1 | 0 | 2000 | 400 | R/W
48144 | HW Comfort add during Heat | Allows the HW Comfort addition to run during heating. |  |  |  |  | 48144 | 48144 | 48144 | 48144 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48145 | HW Comfort mixing valve | Activates the HW Comfort Shunt. |  |  |  |  | 48145 | 48145 | 48145 | 48145 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48146 | HW Comfort mixing valve amp. | Mixing valve amplification for the HW Comfort Accessory |  |  |  |  | 48146 | 48146 | 48146 | 48146 | [5 empty] | s8 | 10 | 1 | 100 | 10 | R/W
48147 | HW Comfort mixing valve wait | Wait time between changes of the mixing valve for the HW Comfort Accessory |  |  |  |  | 48147 | 48147 | 48147 | 48147 |  |  |  |  | secs | s16 | 10 | 10 | 300 | 30 | R/W
48148 | HW Comfort hotwater temperature | The desired hotwater temperature |  |  |  |  | 48148 | 48148 | 48148 | 48148 |  |  |  |  | °C | s8 | 10 | 40 | 65 | 55 | R/W
48156 | External cooling accessory | Activates the external cooling accessory | [9 empty] | 48156 | 48156 | 48156 |  | u8 | 1 | 0 | 1 | 0 | R/W
48157 | HW Comfort add. | Activates the HW Comfort Addition. |  |  |  |  | 48157 | 48157 | 48157 | 48157 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48158 | SAM supply air curve: outdoor temp T3 | The supply air curve is defined by 3 supply air temperatures at 3 different outdoor temperatures T1, T2 and T3. |  |  | 48158 | [9 empty] | °C | s16 | 10 | -400 | 200 | 150 | R/W
48159 | SAM supply air curve: outdoor temp T2 | The supply air curve is defined by 3 supply air temperatures at 3 different outdoor temperatures T1, T2 and T3. |  |  | 48159 | [9 empty] | °C | s16 | 10 | -390 | 190 | 0 | R/W
48160 | SAM supply air curve: outdoor temp T1 | The supply air curve is defined by 3 supply air temperatures at 3 different outdoor temperatures T1, T2 and T3. |  |  | 48160 | [9 empty] | °C | s16 | 10 | -400 | 200 | -150 | R/W
48161 | SAM supply air curve: supply air temp at T3 | The supply air curve is defined by 3 supply air temperatures at 3 different outdoor temperatures T1, T2 and T3. |  |  | 48161 | [9 empty] | °C | s16 | 10 | 160 | 520 | 180 | R/W
48162 | SAM supply air curve: supply air temp at T2 | The supply air curve is defined by 3 supply air temperatures at 3 different outdoor temperatures T1, T2 and T3. |  |  | 48162 | [9 empty] | °C | s16 | 10 | 160 | 520 | 180 | R/W
48163 | SAM supply air curve: supply air temp at T1 | The supply air curve is defined by 3 supply air temperatures at 3 different outdoor temperatures T1, T2 and T3. |  |  | 48163 | [9 empty] | °C | s16 | 10 | 160 | 520 | 180 | R/W
48174 | Min cooling supply temp S4 | Minimum allowed supply temperature during cooling |  |  |  |  | 48174 | 48174 | 48174 | 48174 |  | 48174 | 48174 | 48174 | °C | s8 | 1 | -5 | 30 | 18 | R/W
48175 | Min cooling supply temp S3 | Minimum allowed supply temperature during cooling |  |  |  |  | 48175 | 48175 | 48175 | 48175 |  | 48175 | 48175 | 48175 | °C | s8 | 1 | -5 | 30 | 18 | R/W
48176 | Min cooling supply temp S2 | Minimum allowed supply temperature during cooling |  |  |  |  | 48176 | 48176 | 48176 | 48176 |  | 48176 | 48176 | 48176 | °C | s8 | 1 | -5 | 30 | 18 | R/W
48177 | Min cooling supply temp S1 | Minimum allowed supply temperature during cooling |  |  |  |  | 48177 | 48177 | 48177 | 48177 | 48177 | 48177 | 48177 | 48177 | °C | s8 | 1 | -5 | 30 | 18 | R/W
48181 | Own Cooling Curve P3 | User defined cooling curve point |  |  |  |  | 48181 | 48181 | 48181 | 48181 | 48181 | 48181 | 48181 | 48181 | °C | s8 | 1 | -5 | 40 | 20 | R/W
48185 | Own Cooling Curve P5 | User defined cooling curve point |  |  |  |  | 48185 | 48185 | 48185 | 48185 | 48185 | 48185 | 48185 | 48185 | °C | s8 | 1 | -5 | 40 | 20 | R/W
48186 | Cooling use mix. valve S4 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system |  |  |  |  | 48186 | 48186 | 48186 | 48186 |  | 48186 | 48186 | 48186 |  | u8 | 1 | 0 | 1 | 0 | R/W
48187 | Cooling use mix. valve S3 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system |  |  |  |  | 48187 | 48187 | 48187 | 48187 |  | 48187 | 48187 | 48187 |  | u8 | 1 | 0 | 1 | 0 | R/W
48188 | Cooling use mix. valve S2 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system |  |  |  |  | 48188 | 48188 | 48188 | 48188 |  | 48188 | 48188 | 48188 |  | u8 | 1 | 0 | 1 | 0 | R/W
48189 | Cooling use mix. valve S1 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system |  |  |  |  | 48189 | 48189 | 48189 | 48189 | 48189 | 48189 | 48189 | 48189 |  | u8 | 1 | 0 | 0 | 0 | R/W
48190 | Heatdump mix. valve delay | Mixing valve step delay for the heatdump valve |  |  |  |  | 48190 | 48190 | 48190 | 48190 |  |  |  |  | s | s16 | 1 | 10 | 500 | 30 | R/W
48191 | Heatdump mix. valve amp. | Mixing valve amplification for the heatdump valve |  |  |  |  | 48191 | 48191 | 48191 | 48191 | [5 empty] | s8 | 10 | 1 | 100 | 10 | R/W
48192 | Cooldump mix. valve delay | Mixing valve step delay for the cooldump valve for the ACS-system |  |  |  |  | 48192 | 48192 | 48192 | 48192 |  |  |  |  | s | s16 | 1 | 10 | 500 | 30 | R/W
48193 | Cooldump mix. valve amp. | Mixing valve amplification for the cooldump valve for the ACS-system |  |  |  |  | 48193 | 48193 | 48193 | 48193 | [5 empty] | s8 | 10 | 1 | 100 | 10 | R/W
48194 | ACS accessory | Activate the ACS accessory |  |  |  |  | 48194 | 48194 | 48194 | 48194 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48195 | ACS heat dump 24h-function | [5 empty] | 48195 | 48195 | 48195 | 48195 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48197 | ACS closingtime for cool dump | [5 empty] | 48197 | 48197 | 48197 | 48197 |  |  |  |  | s | u8 | 1 | 0 | 100 | 0 | R/W
48198 | ACS max cprs in active cooling | [6 empty] | 48198 | 48198 | 48198 | [5 empty] | u8 | 1 | 0 | 18 | 18 | R/W
48201 | SCA accessory | Activates the SCA accessory |  |  | 48201 | 48201 | [9 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48206 | Silent Mode Status | 1 = active, 0 = inactive |  |  | 48206 | 48206 |  |  |  |  | 48206 | 48206 | 48206 | 48206 |  | u8 | 1 | 0 | 0 | 0 | R
48207 | Period Cool | [10 empty] | 48207 | 48207 | 48207 | min | u8 | 1 | 0 | 180 | 30 | R/W
48208 | Operational mode cool pump | [11 empty] | 48208 | 48208 |  | u8 | 1 | 0 | 1 | 1 | R/W
48214 | Cooling delta temp. at 20°C | Delta Temperature at 20°C. Used to control charge pump speed | [8 empty] | 48214 | 48214 | 48214 | 48214 | °C | s8 | 1 | 3 | 10 | 3 | R/W
48215 | Cooling delta temp. at 40°C | Delta Temperature at 40°C. Used to control charge pump speed | [8 empty] | 48215 | 48215 | 48215 | 48215 | °C | s8 | 1 | 3 | 20 | 6 | R/W
48228 | Operational mode charge pump S8 | [10 empty] | 48228 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48229 | Operational mode charge pump S7 | [10 empty] | 48229 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48230 | Operational mode charge pump S6 | [10 empty] | 48230 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48231 | Operational mode charge pump S5 | [10 empty] | 48231 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48232 | Operational mode charge pump S4 | [10 empty] | 48232 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48233 | Operational mode charge pump S3 | [10 empty] | 48233 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48234 | Operational mode charge pump S2 | [10 empty] | 48234 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48235 | Operational mode charge pump S1 | [9 empty] | 48235 | 48235 | 48235 |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48264 | Brine shunt accessory | Activates the Brine shunt accessory |  |  |  |  | 48264 | 48264 | 48264 | 48264 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48265 | Brine shunt amplication | The Brine shunt accessory, shunt amplication |  |  |  |  | 48265 | 48265 | 48265 | 48265 | [5 empty] | s8 | 10 | 0 | 100 | 10 | R/W
48266 | Brine shunt wait time | The Brine shunt accessory, wait time |  |  |  |  | 48266 | 48266 | 48266 | 48266 |  |  |  |  | s | s16 | 1 | 10 | 300 | 30 | R/W
48267 | Brine shunt, max brine temp | The Brine shunt accessory, max brine temperature |  |  |  |  | 48267 | 48267 | 48267 | 48267 |  |  |  |  | °C | u8 | 1 | 0 | 30 | 20 | R/W
48274 | Hot Water Stepdiff Compressor | [6 empty] | 48274 | 48274 | 48274 |  | 48274 |  |  |  | s16 | 10 | 0 | 400 | 100 | R/W
48275 | Max charge pump reg speed | Max heat medium pump reg speed |  |  | 48275 | 48275 | 48275 | 48275 | 48275 | 48275 |  |  |  | 48275 | % | u8 | 1 | 50 | 100 | 100 | R/W
48278 | DM start ext. add. | [12 empty] | 48278 |  | s16 | 1 | 50 | 2000 | 1400 | R/W
48279 | Position of Addition | Addition before QN10:0, Addition after QN10:1 | [8 empty] | 48279 | 48279 |  |  |  | u8 | 1 | 0 | 0 | 0 | R/W
48280 | Internal HW add in tank | Internal HW add in tank | [6 empty] | 48280 | 48280 |  | 48280 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48281 | Charge method HW | Heating medium pump control when hot water is charged |  |  |  | 48281 | 48281 | 48281 | 48281 | 48281 |  | 48281 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48282 | SG Ready heating | Sets whether or not SG Ready should affect heating | 48282 | 48282 | 48282 | 48282 | 48282 | 48282 | 48282 | 48282 | 48282 | 48282 | 48282 | 48282 |  | u8 | 1 | 0 | 1 | 1 | R/W
48283 | SG Ready cooling | Sets whether or not SG Ready should affect cooling | 48283 | 48283 | 48283 | 48283 | 48283 | 48283 | 48283 | 48283 | 48283 | 48283 | 48283 | 48283 |  | u8 | 1 | 0 | 1 | 1 | R/W
48284 | SG Ready hot water | Sets whether or not SG Ready should affect hot water | 48284 | 48284 | 48284 | 48284 | 48284 | 48284 | 48284 | 48284 | 48284 | 48284 | 48284 | 48284 |  | u8 | 1 | 0 | 1 | 1 | R/W
48285 | SG Ready pool | Sets whether or not SG Ready should affect pool | 48285 | 48285 | 48285 | 48285 | 48285 | 48285 | 48285 | 48285 | 48285 | 48285 | 48285 | 48285 |  | u8 | 1 | 0 | 1 | 1 | R/W
48286 | Pool 2 Cpr Percentage | [5 empty] | 48286 | [7 empty] | % | u8 | 1 | 1 | 100 | 1 | R/W
48287 | Pool 1 Cpr Percentage | [5 empty] | 48287 | [7 empty] | % | u8 | 1 | 1 | 100 | 1 | R/W
48288 | Cool Cpr Percentage | [5 empty] | 48288 | [7 empty] | % | u8 | 1 | 1 | 100 | 1 | R/W
48367 | Speed circ.pump Heat Slave 8 | [10 empty] | 48367 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48368 | Speed circ.pump Heat Slave 7 | [10 empty] | 48368 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48369 | Speed circ.pump Heat Slave 6 | [10 empty] | 48369 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48370 | Speed circ.pump Heat Slave 5 | [10 empty] | 48370 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48371 | Speed circ.pump Heat Slave 4 | [10 empty] | 48371 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48372 | Speed circ.pump Heat Slave 3 | [10 empty] | 48372 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48373 | Speed circ.pump Heat Slave 2 | [10 empty] | 48373 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48374 | Speed circ.pump Heat Slave 1 | [9 empty] | 48374 | 48374 | 48374 |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48375 | Op mode circ.pump Heat Slave 8 | [10 empty] | 48375 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48376 | Op mode circ.pump Heat Slave 7 | [10 empty] | 48376 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48377 | Op mode circ.pump Heat Slave 6 | [10 empty] | 48377 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48378 | Op mode circ.pump Heat Slave 5 | [10 empty] | 48378 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48379 | Op mode circ.pump Heat Slave 4 | [10 empty] | 48379 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48380 | Op mode circ.pump Heat Slave 3 | [10 empty] | 48380 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48381 | Op mode circ.pump Heat Slave 2 | [10 empty] | 48381 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48382 | Op mode circ.pump Heat Slave 1 | [9 empty] | 48382 | 48382 | 48382 |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48390 | Speed circ.pump HW Slave 1 | [9 empty] | 48390 | 48390 | 48390 |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48391 | Op mode circ.pump HW Slave 8 | [10 empty] | 48391 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48392 | Op mode circ.pump HW Slave 7 | [10 empty] | 48392 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48393 | Op mode circ.pump HW Slave 6 | [10 empty] | 48393 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48394 | Op mode circ.pump HW Slave 5 | [10 empty] | 48394 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48395 | Op mode circ.pump HW Slave 4 | [10 empty] | 48395 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48396 | Op mode circ.pump HW Slave 3 | [10 empty] | 48396 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48397 | Op mode circ.pump HW Slave 2 | [10 empty] | 48397 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48398 | Op mode circ.pump HW Slave 1 | [9 empty] | 48398 | 48398 | 48398 |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48399 | Speed circ.pump Pool Slave 8 | [10 empty] | 48399 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48400 | Speed circ.pump Pool Slave 7 | [10 empty] | 48400 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48401 | Speed circ.pump Pool Slave 6 | [10 empty] | 48401 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48402 | Speed circ.pump Pool Slave 5 | [10 empty] | 48402 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48403 | Speed circ.pump Pool Slave 4 | [10 empty] | 48403 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48404 | Speed circ.pump Pool Slave 3 | [10 empty] | 48404 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48405 | Speed circ.pump Pool Slave 2 | [10 empty] | 48405 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48406 | Speed circ.pump Pool Slave 1 | [10 empty] | 48406 | 48406 |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48407 | Op mode circ.pump Pool Slave 8 | [10 empty] | 48407 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48408 | Op mode circ.pump Pool Slave 7 | [10 empty] | 48408 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48409 | Op mode circ.pump Pool Slave 6 | [10 empty] | 48409 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48410 | Op mode circ.pump Pool Slave 5 | [10 empty] | 48410 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48411 | Op mode circ.pump Pool Slave 4 | [10 empty] | 48411 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48412 | Op mode circ.pump Pool Slave 3 | [10 empty] | 48412 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48413 | Op mode circ.pump Pool Slave 2 | [10 empty] | 48413 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48414 | Op mode circ.pump Pool Slave 1 | [10 empty] | 48414 | 48414 |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48415 | Speed circ.pump Cooling Slave 8 | [10 empty] | 48415 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48416 | Speed circ.pump Cooling Slave 7 | [10 empty] | 48416 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48417 | Speed circ.pump Cooling Slave 6 | [10 empty] | 48417 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48418 | Speed circ.pump Cooling Slave 5 | [10 empty] | 48418 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48419 | Speed circ.pump Cooling Slave 4 | [10 empty] | 48419 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48420 | Speed circ.pump Cooling Slave 3 | [10 empty] | 48420 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48421 | Speed circ.pump Cooling Slave 2 | [10 empty] | 48421 |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48422 | Speed circ.pump Cooling Slave 1 | [9 empty] | 48422 | 48422 | 48422 |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48424 | Op mode circ.pump Cooling Slave 8 | [10 empty] | 48424 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48425 | Op mode circ.pump Cooling Slave 7 | [10 empty] | 48425 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48426 | Op mode circ.pump Cooling Slave 6 | [10 empty] | 48426 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48427 | Op mode circ.pump Cooling Slave 5 | [10 empty] | 48427 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48428 | Op mode circ.pump Cooling Slave 4 | [10 empty] | 48428 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48429 | Op mode circ.pump Cooling Slave 3 | [10 empty] | 48429 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48430 | Op mode circ.pump Cooling Slave 2 | [10 empty] | 48430 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48431 | Op mode circ.pump Cooling Slave 1 | [9 empty] | 48431 | 48431 | 48431 |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48433 | Speed circ.pump Waiting Slave 8 | [10 empty] | 48433 |  |  | % | u8 | 1 | 1 | 100 | 30 | R/W
48434 | Speed circ.pump Waiting Slave 7 | [10 empty] | 48434 |  |  | % | u8 | 1 | 1 | 100 | 30 | R/W
48435 | Speed circ.pump Waiting Slave 6 | [10 empty] | 48435 |  |  | % | u8 | 1 | 1 | 100 | 30 | R/W
48436 | Speed circ.pump Waiting Slave 5 | [10 empty] | 48436 |  |  | % | u8 | 1 | 1 | 100 | 30 | R/W
48437 | Speed circ.pump Waiting Slave 4 | [10 empty] | 48437 |  |  | % | u8 | 1 | 1 | 100 | 30 | R/W
48438 | Speed circ.pump Waiting Slave 3 | [10 empty] | 48438 |  |  | % | u8 | 1 | 1 | 100 | 30 | R/W
48439 | Speed circ.pump Waiting Slave 2 | [10 empty] | 48439 |  |  | % | u8 | 1 | 1 | 100 | 30 | R/W
48440 | Speed circ.pump Waiting Slave 1 | [9 empty] | 48440 | 48440 | 48440 |  | % | u8 | 1 | 1 | 100 | 30 | R/W
48452 | Auto heat medium pump speed, hw | Auto heat medium pump speed hw |  |  | 48452 | 48452 | 48452 | 48452 | 48452 | 48452 |  |  |  |  | % | s8 | 1 | 0 | 1 | 1 | R/W
48453 | Auto heat medium pump speed, heat | Auto heat medium pump speed heat |  |  | 48453 | 48453 | 48453 | 48453 | 48453 | 48453 |  |  |  |  | % | s8 | 1 | 0 | 1 | 1 | R/W
48454 | Auto heat medium pump speed, pool | Auto heat medium pump speed pool |  |  | 48454 | 48454 | 48454 | 48454 | 48454 | 48454 |  |  |  |  | % | s8 | 1 | 0 | 1 | 1 | R/W
48455 | Auto heat medium pump speed, cool | Auto heat medium pump speed cool |  |  | 48455 | 48455 | 48455 | 48455 | 48455 | 48455 |  |  |  |  | % | s8 | 1 | 0 | 1 | 0 | R/W
48456 | Operational mode heat medium pump, cooling | [5 empty] | 48456 | 48456 | 48456 | 48456 | [5 empty] | u8 | 1 | 10 | 20 | 10 | R/W
48457 | Int shunt controlled add. | [7 empty] | 48457 | 48457 |  | 48457 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48458 | Max speed circ.pump Heat | [5 empty] | 48458 | 48458 | 48458 | 48458 |  |  |  |  | % | u8 | 1 | 50 | 100 | 100 | R/W
48459 | Speed brine pump passive cooling | [5 empty] | 48459 | 48459 | 48459 | 48459 |  |  |  |  | % | u8 | 1 | 0 | 100 | 75 | R/W
48460 | EB108 Max charge pump reg speed | Max charge pump reg speed | [9 empty] | 48460 |  |  | % | u8 | 1 | 80 | 100 | 100 | R/W
48461 | EB107 Max charge pump reg speed | Max charge pump reg speed | [9 empty] | 48461 |  |  | % | u8 | 1 | 80 | 100 | 100 | R/W
48462 | EB106 Max charge pump reg speed | Max charge pump reg speed | [9 empty] | 48462 |  |  | % | u8 | 1 | 80 | 100 | 100 | R/W
48463 | EB105 Max charge pump reg speed | Max charge pump reg speed | [9 empty] | 48463 |  |  | % | u8 | 1 | 80 | 100 | 100 | R/W
48464 | EB104 Max charge pump reg speed | Max charge pump reg speed | [9 empty] | 48464 |  |  | % | u8 | 1 | 80 | 100 | 100 | R/W
48465 | EB103 Max charge pump reg speed | Max charge pump reg speed | [9 empty] | 48465 |  |  | % | u8 | 1 | 80 | 100 | 100 | R/W
48466 | EB102 Max charge pump reg speed | Max charge pump reg speed | [9 empty] | 48466 |  |  | % | u8 | 1 | 80 | 100 | 100 | R/W
48467 | EB101 Max charge pump reg speed | Max charge pump reg speed | [8 empty] | 48467 | 48467 | 48467 | 48467 | % | u8 | 1 | 80 | 100 | 100 | R/W
48468 | Operational mode charge pump in cooling mode S8 | [10 empty] | 48468 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48469 | Operational mode charge pump in cooling mode S7 | [10 empty] | 48469 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48470 | Operational mode charge pump in cooling mode S6 | [10 empty] | 48470 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48471 | Operational mode charge pump in cooling mode S5 | [10 empty] | 48471 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48472 | Operational mode charge pump in cooling mode S4 | [10 empty] | 48472 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48473 | Operational mode charge pump in cooling mode S3 | [10 empty] | 48473 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48474 | Operational mode charge pump in cooling mode S2 | [10 empty] | 48474 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48475 | Operational mode charge pump in cooling mode S1 | [9 empty] | 48475 | 48475 | 48475 |  |  | u8 | 1 | 0 | 1 | 1 | R/W
48486 | Prioritize Addition AXC40 | [11 empty] | 48486 | 48486 |  | u8 | 1 | 0 | 1 | 0 | R/W
48487 | Speed Circulation Pump Active Cooling EP14 | [5 empty] | 48487 | 48487 | 48487 | 48487 |  |  |  |  | % | u8 | 1 | 1 | 100 | 70 | R/W
48488 | Heat Curve S6 | Heat curve, see manual for more information | 48488 | 48488 | 48488 | 48488 | 48488 | 48488 | 48488 | 48488 |  | 48488 | 48488 | 48488 |  | s8 | 1 | 0 | 15 | 9 | R/W
48489 | Heat Curve S5 | Heat curve, see manual for more information | 48489 | 48489 | 48489 | 48489 | 48489 | 48489 | 48489 | 48489 |  | 48489 | 48489 | 48489 |  | s8 | 1 | 0 | 15 | 9 | R/W
48491 | Heat Offset S8 | Offset of the heat curve, see manual for more information | 48491 | 48491 | 48491 | 48491 | 48491 | 48491 | 48491 | 48491 |  | 48491 | 48491 | 48491 |  | s8 | 1 | -10 | 10 | 0 | R/W
48492 | Heat Offset S7 | Offset of the heat curve, see manual for more information | 48492 | 48492 | 48492 | 48492 | 48492 | 48492 | 48492 | 48492 |  | 48492 | 48492 | 48492 |  | s8 | 1 | -10 | 10 | 0 | R/W
48493 | Heat Offset S6 | Offset of the heat curve, see manual for more information | 48493 | 48493 | 48493 | 48493 | 48493 | 48493 | 48493 | 48493 |  | 48493 | 48493 | 48493 |  | s8 | 1 | -10 | 10 | 0 | R/W
48494 | Heat Offset S5 | Offset of the heat curve, see manual for more information | 48494 | 48494 | 48494 | 48494 | 48494 | 48494 | 48494 | 48494 |  | 48494 | 48494 | 48494 |  | s8 | 1 | -10 | 10 | 0 | R/W
48495 | Min Supply System 8 |  | 48495 | 48495 | 48495 | 48495 | 48495 | 48495 | 48495 | 48495 |  | 48495 | 48495 | 48495 | °C | s16 | 10 | 50 | 700 | 200 | R/W
48496 | Min Supply System 7 |  | 48496 | 48496 | 48496 | 48496 | 48496 | 48496 | 48496 | 48496 |  | 48496 | 48496 | 48496 | °C | s16 | 10 | 50 | 700 | 200 | R/W
48497 | Min Supply System 6 |  | 48497 | 48497 | 48497 | 48497 | 48497 | 48497 | 48497 | 48497 |  | 48497 | 48497 | 48497 | °C | s16 | 10 | 50 | 700 | 200 | R/W
48498 | Min Supply System 5 |  | 48498 | 48498 | 48498 | 48498 | 48498 | 48498 | 48498 | 48498 |  | 48498 | 48498 | 48498 | °C | s16 | 10 | 50 | 700 | 200 | R/W
48499 | Max Supply System 8 |  | 48499 | 48499 | 48499 | 48499 | 48499 | 48499 | 48499 | 48499 |  | 48499 | 48499 | 48499 | °C | s16 | 10 | 50 | 800 | 600 | R/W
48500 | Max Supply System 7 |  | 48500 | 48500 | 48500 | 48500 | 48500 | 48500 | 48500 | 48500 |  | 48500 | 48500 | 48500 | °C | s16 | 10 | 50 | 800 | 600 | R/W
48501 | Max Supply System 6 |  | 48501 | 48501 | 48501 | 48501 | 48501 | 48501 | 48501 | 48501 |  | 48501 | 48501 | 48501 | °C | s16 | 10 | 50 | 800 | 600 | R/W
48502 | Max Supply System 5 |  | 48502 | 48502 | 48502 | 48502 | 48502 | 48502 | 48502 | 48502 |  | 48502 | 48502 | 48502 | °C | s16 | 10 | 50 | 800 | 600 | R/W
48503 | External adjustment S8 | Change of the offset of the heat curve when closing the external adjustment input | 48503 | 48503 | 48503 | 48503 | 48503 | 48503 | 48503 | 48503 |  | 48503 | 48503 | 48503 |  | s8 | 1 | -10 | 10 | 0 | R/W
48504 | External adjustment S7 | Change of the offset of the heat curve when closing the external adjustment input | 48504 | 48504 | 48504 | 48504 | 48504 | 48504 | 48504 | 48504 |  | 48504 | 48504 | 48504 |  | s8 | 1 | -10 | 10 | 0 | R/W
48505 | External adjustment S6 | Change of the offset of the heat curve when closing the external adjustment input | 48505 | 48505 | 48505 | 48505 | 48505 | 48505 | 48505 | 48505 |  | 48505 | 48505 | 48505 |  | s8 | 1 | -10 | 10 | 0 | R/W
48506 | External adjustment S5 | Change of the offset of the heat curve when closing the external adjustment input | 48506 | 48506 | 48506 | 48506 | 48506 | 48506 | 48506 | 48506 |  | 48506 | 48506 | 48506 |  | s8 | 1 | -10 | 10 | 0 | R/W
48507 | External adjustment with room sensor S8 | Room temperature setting when closing the external adjustment input | 48507 | 48507 | 48507 | 48507 | 48507 | 48507 | 48507 | 48507 |  | 48507 | 48507 | 48507 | °C | s16 | 10 | 50 | 300 | 200 | R/W
48508 | External adjustment with room sensor S7 | Room temperature setting when closing the external adjustment input | 48508 | 48508 | 48508 | 48508 | 48508 | 48508 | 48508 | 48508 |  | 48508 | 48508 | 48508 | °C | s16 | 10 | 50 | 300 | 200 | R/W
48509 | External adjustment with room sensor S6 | Room temperature setting when closing the external adjustment input | 48509 | 48509 | 48509 | 48509 | 48509 | 48509 | 48509 | 48509 |  | 48509 | 48509 | 48509 | °C | s16 | 10 | 50 | 300 | 200 | R/W
48510 | External adjustment with room sensor S5 | Room temperature setting when closing the external adjustment input | 48510 | 48510 | 48510 | 48510 | 48510 | 48510 | 48510 | 48510 |  | 48510 | 48510 | 48510 | °C | s16 | 10 | 50 | 300 | 200 | R/W
48567 | Initiate inverter | Start initiation process of the inverter |  |  | 48567 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R/W
48568 | Force inverter init | Force inverter initiation process of the inverter |  |  | 48568 | [10 empty] | u8 | 1 | 0 | 0 | 0 | R/W
48569 | Climate system 5 accessory | Activates the climate system 5 accessory | 48569 | 48569 | 48569 | 48569 | 48569 | 48569 | 48569 | 48569 |  | 48569 | 48569 | 48569 |  | u8 | 1 | 0 | 1 | 0 | R/W
48570 | Climate system 6 accessory | Activates the climate system 6 accessory | 48570 | 48570 | 48570 | 48570 | 48570 | 48570 | 48570 | 48570 |  | 48570 | 48570 | 48570 |  | u8 | 1 | 0 | 1 | 0 | R/W
48571 | Climate system 7 accessory | Activates the climate system 7 accessory | 48571 | 48571 | 48571 | 48571 | 48571 | 48571 | 48571 | 48571 |  | 48571 | 48571 | 48571 |  | u8 | 1 | 0 | 1 | 0 | R/W
48572 | Climate system 8 accessory | Activates the climate system 8 accessory | 48572 | 48572 | 48572 | 48572 | 48572 | 48572 | 48572 | 48572 |  | 48572 | 48572 | 48572 |  | u8 | 1 | 0 | 1 | 0 | R/W
48573 | Climate system 8 mixing valve amp. | Mixing valve amplification for extra climate systems | 48573 | 48573 | 48573 | 48573 | 48573 | 48573 | 48573 | 48573 |  | 48573 | 48573 | 48573 |  | s8 | 10 | 1 | 100 | 10 | R/W
48574 | Climate system 7 mixing valve amp. | Mixing valve amplification for extra climate systems | 48574 | 48574 | 48574 | 48574 | 48574 | 48574 | 48574 | 48574 |  | 48574 | 48574 | 48574 |  | s8 | 10 | 1 | 100 | 10 | R/W
48575 | Climate system 6 mixing valve amp. | Mixing valve amplification for extra climate systems | 48575 | 48575 | 48575 | 48575 | 48575 | 48575 | 48575 | 48575 |  | 48575 | 48575 | 48575 |  | s8 | 10 | 1 | 100 | 10 | R/W
48576 | Climate system 5 mixing valve amp. | Mixing valve amplification for extra climate systems | 48576 | 48576 | 48576 | 48576 | 48576 | 48576 | 48576 | 48576 |  | 48576 | 48576 | 48576 |  | s8 | 10 | 1 | 100 | 10 | R/W
48577 | Climate system 8 shunt wait | Wait time between changes of the shunt in extra climate systems | 48577 | 48577 | 48577 | 48577 | 48577 | 48577 | 48577 | 48577 |  | 48577 | 48577 | 48577 | secs | s16 | 10 | 10 | 300 | 30 | R/W
48578 | Climate system 7 shunt wait | Wait time between changes of the shunt in extra climate systems | 48578 | 48578 | 48578 | 48578 | 48578 | 48578 | 48578 | 48578 |  | 48578 | 48578 | 48578 | secs | s16 | 10 | 10 | 300 | 30 | R/W
48579 | Climate system 6 shunt wait | Wait time between changes of the shunt in extra climate systems | 48579 | 48579 | 48579 | 48579 | 48579 | 48579 | 48579 | 48579 |  | 48579 | 48579 | 48579 | secs | s16 | 10 | 10 | 300 | 30 | R/W
48580 | Climate system 5 shunt wait | Wait time between changes of the shunt in extra climate systems | 48580 | 48580 | 48580 | 48580 | 48580 | 48580 | 48580 | 48580 |  | 48580 | 48580 | 48580 | secs | s16 | 10 | 10 | 300 | 30 | R/W
48581 | Min cooling supply temp S8 | Minimum allowed supply temperature during cooling |  |  |  |  | 48581 | 48581 | 48581 | 48581 |  | 48581 | 48581 | 48581 | °C | s8 | 1 | -5 | 30 | 18 | R/W
48582 | Min cooling supply temp S7 | Minimum allowed supply temperature during cooling |  |  |  |  | 48582 | 48582 | 48582 | 48582 |  | 48582 | 48582 | 48582 | °C | s8 | 1 | -5 | 30 | 18 | R/W
48583 | Min cooling supply temp S6 | Minimum allowed supply temperature during cooling |  |  |  |  | 48583 | 48583 | 48583 | 48583 |  | 48583 | 48583 | 48583 | °C | s8 | 1 | -5 | 30 | 18 | R/W
48584 | Min cooling supply temp S5 | Minimum allowed supply temperature during cooling |  |  |  |  | 48584 | 48584 | 48584 | 48584 |  | 48584 | 48584 | 48584 | °C | s8 | 1 | -5 | 30 | 18 | R/W
48593 | Cooling use mix. valve S8 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system |  |  |  |  | 48593 | 48593 | 48593 | 48593 |  | 48593 | 48593 | 48593 |  | u8 | 1 | 0 | 1 | 0 | R/W
48594 | Cooling use mix. valve S7 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system |  |  |  |  | 48594 | 48594 | 48594 | 48594 |  | 48594 | 48594 | 48594 |  | u8 | 1 | 0 | 1 | 0 | R/W
48595 | Cooling use mix. valve S6 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system |  |  |  |  | 48595 | 48595 | 48595 | 48595 |  | 48595 | 48595 | 48595 |  | u8 | 1 | 0 | 1 | 0 | R/W
48596 | Cooling use mix. valve S5 | Sets if the valve should be used or not in cooling mode. Only applies if cooling is available in the system |  |  |  |  | 48596 | 48596 | 48596 | 48596 |  | 48596 | 48596 | 48596 |  | u8 | 1 | 0 | 1 | 0 | R/W
48597 | Heating use mix. valve S8 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. |  |  |  |  | 48597 | 48597 | 48597 | 48597 |  | 48597 | 48597 | 48597 |  | u8 | 1 | 0 | 1 | 1 | R/W
48598 | Heating use mix. valve S7 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. |  |  |  |  | 48598 | 48598 | 48598 | 48598 |  | 48598 | 48598 | 48598 |  | u8 | 1 | 0 | 1 | 1 | R/W
48599 | Heating use mix. valve S6 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. |  |  |  |  | 48599 | 48599 | 48599 | 48599 |  | 48599 | 48599 | 48599 |  | u8 | 1 | 0 | 1 | 1 | R/W
48600 | Heating use mix. valve S5 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. |  |  |  |  | 48600 | 48600 | 48600 | 48600 |  | 48600 | 48600 | 48600 |  | u8 | 1 | 0 | 1 | 1 | R/W
48601 | Heating use mix. valve S4 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. |  |  |  |  | 48601 | 48601 | 48601 | 48601 |  | 48601 | 48601 | 48601 |  | u8 | 1 | 0 | 1 | 1 | R/W
48602 | Heating use mix. valve S3 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. |  |  |  |  | 48602 | 48602 | 48602 | 48602 |  | 48602 | 48602 | 48602 |  | u8 | 1 | 0 | 1 | 1 | R/W
48603 | Heating use mix. valve S2 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. |  |  |  |  | 48603 | 48603 | 48603 | 48603 |  | 48603 | 48603 | 48603 |  | u8 | 1 | 0 | 1 | 1 | R/W
48604 | Heating use mix. valve S1 | Sets if the valve should be used or not in heating mode. Only applies if cooling is available in the system. Otherwise the valve is always used in heating mode. |  |  |  |  | 48604 | 48604 | 48604 | 48604 | 48604 | 48604 | 48604 | 48604 |  | u8 | 1 | 0 | 1 | 1 | R/W
48607 | ERS 1 accessory | Activates the ERS accessory |  |  |  |  | 48607 | 48607 | 48607 | 48607 |  | 48607 | 48607 | 48607 |  | u8 | 1 | 0 | 1 | 0 | R/W
48637 | AHPS docking accessory | 0=not activated, 1=activated |  |  | 48637 | [10 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48638 | AHPS docking: solar heating | The specific AHPS docking: 0=not activated, 1=activated |  |  | 48638 | [10 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48639 | AHPS docking: prioritized add. | The specific AHPS docking: 0=not activated, 1=activated |  |  | 48639 | [10 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48640 | AHPS docking: ext. addition | The specific AHPS docking: 0=not activated, 1=activated |  |  | 48640 | [10 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48641 | AHPS docking: ext. hot water | The specific AHPS docking: 0=not activated, 1=activated |  |  | 48641 | [10 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48647 | EB103/104-GP12 | Activates the EB103/104-GP12 Accessory. | [9 empty] | 48647 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48648 | EB105/106-GP12 | Activates the EB105/106-GP12 Accessory. | [9 empty] | 48648 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48649 | EB107/108-GP12 | Activates the EB107/108-GP12 Accessory. | [9 empty] | 48649 |  |  |  | u8 | 1 | 0 | 1 | 0 | R/W
48659 | Cut off frequency activated 2 | Cut off frequency activated |  |  | 48659 | 48659 | 48659 | [8 empty] | s8 | 1 | 0 | 1 | 0 | R/W
48660 | Cut off frequency activated 1 | Cut off frequency activated |  |  | 48660 | 48660 | 48660 | [8 empty] | s8 | 1 | 0 | 1 | 0 | R/W
48661 | Cut off frequency start 2 | Cut off frequency start |  |  | 48661 | 48661 | 48661 | [7 empty] | Hz | u8 | 1 | 17 | 115 | 17 | R/W
48662 | Cut off frequency start 1 | Cut off frequency start |  |  | 48662 | 48662 | 48662 | [7 empty] | Hz | u8 | 1 | 17 | 115 | 17 | R/W
48663 | Cut off frequency stop 2 | Cut off frequency stop |  |  | 48663 | 48663 | 48663 | [7 empty] | Hz | u8 | 1 | 22 | 120 | 22 | R/W
48664 | Cut off frequency stop 1 | Cut off frequency stop |  |  | 48664 | 48664 | 48664 | [7 empty] | Hz | u8 | 1 | 22 | 120 | 22 | R/W
48675 | Use room sensor S8 | When activated the system uses the room sensor | 48675 | 48675 | 48675 | 48675 | 48675 | 48675 | 48675 | 48675 |  | 48675 | 48675 | 48675 |  | u8 | 1 | 0 | 1 | 0 | R/W
48676 | Use room sensor S7 | When activated the system uses the room sensor | 48676 | 48676 | 48676 | 48676 | 48676 | 48676 | 48676 | 48676 |  | 48676 | 48676 | 48676 |  | u8 | 1 | 0 | 1 | 0 | R/W
48677 | Use room sensor S6 | When activated the system uses the room sensor | 48677 | 48677 | 48677 | 48677 | 48677 | 48677 | 48677 | 48677 |  | 48677 | 48677 | 48677 |  | u8 | 1 | 0 | 1 | 0 | R/W
48678 | Use room sensor S5 | When activated the system uses the room sensor | 48678 | 48678 | 48678 | 48678 | 48678 | 48678 | 48678 | 48678 |  | 48678 | 48678 | 48678 |  | u8 | 1 | 0 | 1 | 0 | R/W
48680 | Room sensor setpoint S8 | Sets the room temperature setpoint for the system | 48680 | 48680 | 48680 | 48680 | 48680 | 48680 | 48680 | 48680 |  | 48680 | 48680 | 48680 | °C | s16 | 10 | 50 | 300 | 200 | R/W
48681 | Room sensor setpoint S7 | Sets the room temperature setpoint for the system | 48681 | 48681 | 48681 | 48681 | 48681 | 48681 | 48681 | 48681 |  | 48681 | 48681 | 48681 | °C | s16 | 10 | 50 | 300 | 200 | R/W
48682 | Room sensor setpoint S6 | Sets the room temperature setpoint for the system | 48682 | 48682 | 48682 | 48682 | 48682 | 48682 | 48682 | 48682 |  | 48682 | 48682 | 48682 | °C | s16 | 10 | 50 | 300 | 200 | R/W
48683 | Room sensor setpoint S5 | Sets the room temperature setpoint for the system | 48683 | 48683 | 48683 | 48683 | 48683 | 48683 | 48683 | 48683 |  | 48683 | 48683 | 48683 | °C | s16 | 10 | 50 | 300 | 200 | R/W
48685 | Room sensor factor S8 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 48685 | 48685 | 48685 | 48685 | 48685 | 48685 | 48685 | 48685 |  | 48685 | 48685 | 48685 |  | u8 | 10 | 0 | 60 | 10 | R/W
48686 | Room sensor factor S7 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 48686 | 48686 | 48686 | 48686 | 48686 | 48686 | 48686 | 48686 |  | 48686 | 48686 | 48686 |  | u8 | 10 | 0 | 60 | 10 | R/W
48687 | Room sensor factor S6 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 48687 | 48687 | 48687 | 48687 | 48687 | 48687 | 48687 | 48687 |  | 48687 | 48687 | 48687 |  | u8 | 10 | 0 | 60 | 10 | R/W
48688 | Room sensor factor S5 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 48688 | 48688 | 48688 | 48688 | 48688 | 48688 | 48688 | 48688 |  | 48688 | 48688 | 48688 |  | u8 | 10 | 0 | 60 | 10 | R/W
48724 | Cool curve S8 | Cool curve, see manual for more information |  |  |  |  | 48724 | 48724 | 48724 | 48724 |  | 48724 | 48724 | 48724 |  | s8 | 1 | 0 | 9 | 0 | R/W
48725 | Cool curve S7 | Cool curve, see manual for more information |  |  |  |  | 48725 | 48725 | 48725 | 48725 |  | 48725 | 48725 | 48725 |  | s8 | 1 | 0 | 9 | 0 | R/W
48726 | Cool curve S6 | Cool curve, see manual for more information |  |  |  |  | 48726 | 48726 | 48726 | 48726 |  | 48726 | 48726 | 48726 |  | s8 | 1 | 0 | 9 | 0 | R/W
48727 | Cool curve S5 | Cool curve, see manual for more information |  |  |  |  | 48727 | 48727 | 48727 | 48727 |  | 48727 | 48727 | 48727 |  | s8 | 1 | 0 | 9 | 0 | R/W
48728 | Cool curve S4 | Cool curve, see manual for more information |  |  |  |  | 48728 | 48728 | 48728 | 48728 |  | 48728 | 48728 | 48728 |  | s8 | 1 | 0 | 9 | 0 | R/W
48729 | Cool curve S3 | Cool curve, see manual for more information |  |  |  |  | 48729 | 48729 | 48729 | 48729 |  | 48729 | 48729 | 48729 |  | s8 | 1 | 0 | 9 | 0 | R/W
48730 | Cool curve S2 | Cool curve, see manual for more information |  |  |  |  | 48730 | 48730 | 48730 | 48730 |  | 48730 | 48730 | 48730 |  | s8 | 1 | 0 | 9 | 0 | R/W
48731 | Cool curve S1 | Cool curve, see manual for more information |  |  |  |  | 48731 | 48731 | 48731 | 48731 | 48731 | 48731 | 48731 | 48731 |  | s8 | 1 | 0 | 9 | 0 | R/W
48732 | Cool offset S8 | Offset of the cool curve, see manual for more information | 48732 | 48732 | 48732 | 48732 | 48732 | 48732 | 48732 | 48732 | 48732 | 48732 | 48732 | 48732 |  | s8 | 1 | -10 | 10 | 0 | R/W
48733 | Cool offset S7 | Offset of the cool curve, see manual for more information | 48733 | 48733 | 48733 | 48733 | 48733 | 48733 | 48733 | 48733 | 48733 | 48733 | 48733 | 48733 |  | s8 | 1 | -10 | 10 | 0 | R/W
48734 | Cool offset S6 | Offset of the cool curve, see manual for more information | 48734 | 48734 | 48734 | 48734 | 48734 | 48734 | 48734 | 48734 | 48734 | 48734 | 48734 | 48734 |  | s8 | 1 | -10 | 10 | 0 | R/W
48735 | Cool offset S5 | Offset of the cool curve, see manual for more information | 48735 | 48735 | 48735 | 48735 | 48735 | 48735 | 48735 | 48735 | 48735 | 48735 | 48735 | 48735 |  | s8 | 1 | -10 | 10 | 0 | R/W
48736 | Cool offset S4 | Offset of the cool curve, see manual for more information | 48736 | 48736 | 48736 | 48736 | 48736 | 48736 | 48736 | 48736 | 48736 | 48736 | 48736 | 48736 |  | s8 | 1 | -10 | 10 | 0 | R/W
48737 | Cool offset S3 | Offset of the cool curve, see manual for more information | 48737 | 48737 | 48737 | 48737 | 48737 | 48737 | 48737 | 48737 | 48737 | 48737 | 48737 | 48737 |  | s8 | 1 | -10 | 10 | 0 | R/W
48738 | Cool offset S2 | Offset of the cool curve, see manual for more information | 48738 | 48738 | 48738 | 48738 | 48738 | 48738 | 48738 | 48738 | 48738 | 48738 | 48738 | 48738 |  | s8 | 1 | -10 | 10 | 0 | R/W
48739 | Cool offset S1 | Offset of the cool curve, see manual for more information | 48739 | 48739 | 48739 | 48739 | 48739 | 48739 | 48739 | 48739 | 48739 | 48739 | 48739 | 48739 |  | s8 | 1 | -10 | 10 | 0 | R/W
48740 | Own Cooling Curve P4 | User defined cooling curve point |  |  |  |  | 48740 | 48740 | 48740 | 48740 | 48740 | 48740 | 48740 | 48740 | °C | s8 | 1 | -5 | 40 | 20 | R/W
48741 | Own Cooling Curve P2 | User defined cooling curve point |  |  |  |  | 48741 | 48741 | 48741 | 48741 | 48741 | 48741 | 48741 | 48741 | °C | s8 | 1 | -5 | 40 | 20 | R/W
48742 | Own Cooling Curve P1 | User defined cooling curve point |  |  |  |  | 48742 | 48742 | 48742 | 48742 | 48742 | 48742 | 48742 | 48742 | °C | s8 | 1 | -5 | 40 | 20 | R/W
48743 | Hot water high power mode |  |  |  | 48743 | 48743 | 48743 |  | 48743 |  | 48743 | 48743 | 48743 | 48743 |  | s8 | 1 | 0 | 1 | 0 | R/W
48755 | Transformer ratio | Ratio of the current measurement transformers | 48755 | 48755 | 48755 | 48755 | 48755 | 48755 | 48755 | 48755 |  | 48755 | 48755 | 48755 |  | u16 | 1 | 300 | 2500 | 300 | R/W
48778 | Room sensor cool setpoint S8 | Sets the room temperature setpoint for the system in cooling mode |  |  |  |  | 48778 | 48778 | 48778 | 48778 |  | 48778 | 48778 | 48778 | °C | s16 | 10 | 50 | 350 | 250 | R/W
48779 | Room sensor cool setpoint S7 | Sets the room temperature setpoint for the system in cooling mode |  |  |  |  | 48779 | 48779 | 48779 | 48779 |  | 48779 | 48779 | 48779 | °C | s16 | 10 | 50 | 350 | 250 | R/W
48780 | Room sensor cool setpoint S6 | Sets the room temperature setpoint for the system in cooling mode |  |  |  |  | 48780 | 48780 | 48780 | 48780 |  | 48780 | 48780 | 48780 | °C | s16 | 10 | 50 | 350 | 250 | R/W
48781 | Room sensor cool setpoint S5 | Sets the room temperature setpoint for the system in cooling mode |  |  |  |  | 48781 | 48781 | 48781 | 48781 |  | 48781 | 48781 | 48781 | °C | s16 | 10 | 50 | 350 | 250 | R/W
48782 | Room sensor cool setpoint S4 | Sets the room temperature setpoint for the system in cooling mode |  |  |  |  | 48782 | 48782 | 48782 | 48782 |  | 48782 | 48782 | 48782 | °C | s16 | 10 | 50 | 350 | 250 | R/W
48783 | Room sensor cool setpoint S3 | Sets the room temperature setpoint for the system in cooling mode |  |  |  |  | 48783 | 48783 | 48783 | 48783 |  | 48783 | 48783 | 48783 | °C | s16 | 10 | 50 | 350 | 250 | R/W
48784 | Room sensor cool setpoint S2 | Sets the room temperature setpoint for the system in cooling mode |  |  |  |  | 48784 | 48784 | 48784 | 48784 |  | 48784 | 48784 | 48784 | °C | s16 | 10 | 50 | 350 | 250 | R/W
48785 | Room sensor cool setpoint S1 | Sets the room temperature setpoint for the system in cooling mode |  |  |  |  | 48785 | 48785 | 48785 | 48785 | 48785 | 48785 | 48785 | 48785 | °C | s16 | 10 | 50 | 350 | 250 | R/W
48786 | Room sensor cool factor S8 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. |  |  |  |  | 48786 | 48786 | 48786 | 48786 |  | 48786 | 48786 | 48786 |  | u8 | 10 | 0 | 60 | 10 | R/W
48787 | Room sensor cool factor S7 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. |  |  |  |  | 48787 | 48787 | 48787 | 48787 |  | 48787 | 48787 | 48787 |  | u8 | 10 | 0 | 60 | 10 | R/W
48788 | Room sensor cool factor S6 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. |  |  |  |  | 48788 | 48788 | 48788 | 48788 |  | 48788 | 48788 | 48788 |  | u8 | 10 | 0 | 60 | 10 | R/W
48789 | Room sensor cool factor S5 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. |  |  |  |  | 48789 | 48789 | 48789 | 48789 |  | 48789 | 48789 | 48789 |  | u8 | 10 | 0 | 60 | 10 | R/W
48790 | Room sensor cool factor S4 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. |  |  |  |  | 48790 | 48790 | 48790 | 48790 |  | 48790 | 48790 | 48790 |  | u8 | 10 | 0 | 60 | 10 | R/W
48791 | Room sensor cool factor S3 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. |  |  |  |  | 48791 | 48791 | 48791 | 48791 |  | 48791 | 48791 | 48791 |  | u8 | 10 | 0 | 60 | 10 | R/W
48792 | Room sensor cool factor S2 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. |  |  |  |  | 48792 | 48792 | 48792 | 48792 |  | 48792 | 48792 | 48792 |  | u8 | 10 | 0 | 60 | 10 | R/W
48793 | Room sensor cool factor S1 | Setting of how much the difference between set and actual room temperature should affect the supply temperature in cooling mode. |  |  |  |  | 48793 | 48793 | 48793 | 48793 | 48793 | 48793 | 48793 | 48793 |  | u8 | 10 | 0 | 60 | 10 | R/W
48794 | RH set value | RH set value | 48794 | 48794 | 48794 | 48794 | 48794 | 48794 | 48794 | 48794 | 48794 | 48794 | 48794 | 48794 | % | s8 | 1 | 30 | 90 | 60 | R/W
48808 | HTS accessory | HTS accessory |  |  |  |  | 48808 | 48808 | 48808 | 48808 |  | 48808 | 48808 | 48808 |  | u8 | 1 | 0 | 1 | 0 | R/W
48810 | Prevent humidity S8 |  | 48810 | 48810 | 48810 | 48810 | 48810 | 48810 | 48810 | 48810 | 48810 | 48810 | 48810 | 48810 |  | s8 | 1 | 0 | 1 | 0 | R/W
48811 | Prevent humidity S7 |  | 48811 | 48811 | 48811 | 48811 | 48811 | 48811 | 48811 | 48811 | 48811 | 48811 | 48811 | 48811 |  | s8 | 1 | 0 | 1 | 0 | R/W
48812 | Prevent humidity S6 |  | 48812 | 48812 | 48812 | 48812 | 48812 | 48812 | 48812 | 48812 | 48812 | 48812 | 48812 | 48812 |  | s8 | 1 | 0 | 1 | 0 | R/W
48813 | Prevent humidity S5 |  | 48813 | 48813 | 48813 | 48813 | 48813 | 48813 | 48813 | 48813 | 48813 | 48813 | 48813 | 48813 |  | s8 | 1 | 0 | 1 | 0 | R/W
48814 | Prevent humidity S4 |  | 48814 | 48814 | 48814 | 48814 | 48814 | 48814 | 48814 | 48814 | 48814 | 48814 | 48814 | 48814 |  | s8 | 1 | 0 | 1 | 0 | R/W
48815 | Prevent humidity S3 |  | 48815 | 48815 | 48815 | 48815 | 48815 | 48815 | 48815 | 48815 | 48815 | 48815 | 48815 | 48815 |  | s8 | 1 | 0 | 1 | 0 | R/W
48816 | Prevent humidity S2 |  | 48816 | 48816 | 48816 | 48816 | 48816 | 48816 | 48816 | 48816 | 48816 | 48816 | 48816 | 48816 |  | s8 | 1 | 0 | 1 | 0 | R/W
48817 | Prevent humidity S1 |  | 48817 | 48817 | 48817 | 48817 | 48817 | 48817 | 48817 | 48817 | 48817 | 48817 | 48817 | 48817 |  | s8 | 1 | 0 | 1 | 0 | R/W
48819 | Limit humidity in room, heating S8 | Limit humidity in room, heating |  |  |  |  | 48819 | 48819 | 48819 | 48819 |  | 48819 | 48819 | 48819 |  | s8 | 1 | 0 | 1 | 0 | R/W
48820 | Limit humidity in room, heating S7 | Limit humidity in room, heating |  |  |  |  | 48820 | 48820 | 48820 | 48820 |  | 48820 | 48820 | 48820 |  | s8 | 1 | 0 | 1 | 0 | R/W
48821 | Limit humidity in room, heating S6 | Limit humidity in room, heating |  |  |  |  | 48821 | 48821 | 48821 | 48821 |  | 48821 | 48821 | 48821 |  | s8 | 1 | 0 | 1 | 0 | R/W
48822 | Limit humidity in room, heating S5 | Limit humidity in room, heating |  |  |  |  | 48822 | 48822 | 48822 | 48822 |  | 48822 | 48822 | 48822 |  | s8 | 1 | 0 | 1 | 0 | R/W
48823 | Limit humidity in room, heating S4 | Limit humidity in room, heating |  |  |  |  | 48823 | 48823 | 48823 | 48823 |  | 48823 | 48823 | 48823 |  | s8 | 1 | 0 | 1 | 0 | R/W
48824 | Limit humidity in room, heating S3 | Limit humidity in room, heating |  |  |  |  | 48824 | 48824 | 48824 | 48824 |  | 48824 | 48824 | 48824 |  | s8 | 1 | 0 | 1 | 0 | R/W
48825 | Limit humidity in room, heating S2 | Limit humidity in room, heating |  |  |  |  | 48825 | 48825 | 48825 | 48825 |  | 48825 | 48825 | 48825 |  | s8 | 1 | 0 | 1 | 0 | R/W
48826 | Limit humidity in room, heating S1 | Limit humidity in room, heating |  |  |  |  | 48826 | 48826 | 48826 | 48826 |  | 48826 | 48826 | 48826 |  | s8 | 1 | 0 | 1 | 0 | R/W
48828 | OPT | Activates the OPT Accessory. |  |  |  |  | 48828 | 48828 | 48828 | 48828 |  | 48828 | 48828 | 48828 |  | u8 | 1 | 0 | 1 | 0 | R/W
48829 | OPT DM startdiff | The number of degree minutes below the last compressor the OPT is allowed to start |  |  |  |  | 48829 | 48829 | 48829 | 48829 |  | 48829 | 48829 | 48829 |  | s16 | 1 | 10 | 2000 | 700 | R/W
48849 | Speed brine pump active cooling | [5 empty] | 48849 | 48849 | 48849 | 48849 |  |  |  |  | % | u8 | 1 | 0 | 100 | 75 | R/W
48850 | Delta brine pump active cooling | [5 empty] | 48850 | 48850 | 48850 | 48850 |  |  |  |  | °C | u8 | 1 | 2 | 10 | 5 | R/W
48851 | Waiting speed brine pump cooling | [5 empty] | 48851 | 48851 | 48851 | 48851 |  |  |  |  | % | u8 | 1 | 0 | 100 | 30 | R/W
48852 | Modbus40 Word Swap | If set; swapping the words in 32-bit variables when value requested via ''read holding register'' commando. | 48852 | 48852 | 48852 |  | 48852 | 48852 | 48852 | 48852 |  | 48852 | 48852 | 48852 |  | u8 | 1 | 0 | 1 | 1 | R/W
48853 | ERS 1 Exhaust Fan speed 4 | [5 empty] | 48853 | 48853 | 48853 | 48853 |  | 48853 | 48853 | 48853 | % | u8 | 1 | 0 | 100 | 100 | R/W
48854 | ERS 1 Exhaust Fan speed 3 | [5 empty] | 48854 | 48854 | 48854 | 48854 |  | 48854 | 48854 | 48854 | % | u8 | 1 | 0 | 100 | 80 | R/W
48855 | ERS 1 Exhaust Fan speed 2 | [5 empty] | 48855 | 48855 | 48855 | 48855 |  | 48855 | 48855 | 48855 | % | u8 | 1 | 0 | 100 | 30 | R/W
48856 | ERS 1 Exhaust Fan speed 1 | [5 empty] | 48856 | 48856 | 48856 | 48856 |  | 48856 | 48856 | 48856 | % | u8 | 1 | 0 | 100 | 0 | R/W
48857 | ERS 1 Exhaust Fan speed normal | [5 empty] | 48857 | 48857 | 48857 | 48857 |  | 48857 | 48857 | 48857 | % | u8 | 1 | 1 | 100 | 75 | R/W
48858 | ACS Thermostat accessory | Activate the ACS thermostat accessory | [5 empty] | 48858 | 48858 | 48858 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48859 | Filter time BT64 | ACS thermostate BT64 filter time | [5 empty] | 48859 | 48859 | 48859 |  |  |  |  | min | u8 | 1 | 5 | 30 | 5 | R/W
48860 | ACS-therm, Hyst between cpr | ACS thermosate, Hysteresis between cpr | [5 empty] | 48860 | 48860 | 48860 |  |  |  |  | °C | s8 | 1 | 1 | 10 | 2 | R/W
48861 | ACS-therm start temp. | ACS thermostate start temp. | [5 empty] | 48861 | 48861 | 48861 |  |  |  |  | °C | s8 | 1 | -8 | 30 | 10 | R/W
48862 | temp, shift to borehole | ACS thermostate temperature to shift to borehole | [5 empty] | 48862 | 48862 | 48862 |  |  |  |  | °C | s8 | 1 | -8 | 30 | 0 | R/W
48889 | MODBUS40 Disable LOG.SET | If set, the system will ignore the existing LOG.SET on the USB stick.1=ignore LOG.SET,0=use LOG.SET | 48889 | 48889 | 48889 |  | 48889 | 48889 | 48889 | 48889 |  | 48889 | 48889 | 48889 |  | u8 | 1 | 0 | 1 | 0 | R/W
48890 | Outdoor Air Fan Speed |  |  |  |  | 48890 | [8 empty] | % | u8 | 1 | 10 | 100 | 100 | R/W
48891 | Setting up ventilation | Setting up ventilation for normal speed. |  |  | 48891 | 48891 | [9 empty] | u8 | 1 | 0 | 0 | 0 | R/W
48892 | Setting up ventilation, OA mixing | Setting up ventilation for outdoor air mixing when used. |  |  |  | 48892 | [9 empty] | u8 | 1 | 0 | 0 | 0 | R/W
48893 | F135 Heat pump | 0=not activated, 1=activated | [9 empty] | 48893 | 48893 | 48893 |  | u8 | 1 | 0 | 1 | 0 | R/W
48894 | F135 Pump Speed | [10 empty] | 48894 | 48894 | 48894 | % | u8 | 1 | 1 | 100 | 70 | R/W
48895 | F135 HW-Cool | If activated, F135 will take care of all the hot water need when cooling is running | [9 empty] | 48895 | 48895 | 48895 |  | u8 | 1 | 0 | 1 | 0 | R/W
48896 | ERS 1 Supply Fan speed 4 | [5 empty] | 48896 | 48896 | 48896 | 48896 |  | 48896 | 48896 | 48896 | % | u8 | 1 | 0 | 100 | 100 | R/W
48897 | ERS 1 Supply Fan speed 3 | [5 empty] | 48897 | 48897 | 48897 | 48897 |  | 48897 | 48897 | 48897 | % | u8 | 1 | 0 | 100 | 80 | R/W
48898 | ERS 1 Supply Fan speed 2 | [5 empty] | 48898 | 48898 | 48898 | 48898 |  | 48898 | 48898 | 48898 | % | u8 | 1 | 0 | 100 | 30 | R/W
48899 | ERS 1 Supply Fan speed 1 | [5 empty] | 48899 | 48899 | 48899 | 48899 |  | 48899 | 48899 | 48899 | % | u8 | 1 | 0 | 100 | 0 | R/W
48900 | ERS 1 Supply Fan speed normal | [5 empty] | 48900 | 48900 | 48900 | 48900 |  | 48900 | 48900 | 48900 | % | u8 | 1 | 1 | 100 | 75 | R/W
48901 | External ERS 1 accessory min exhaust temp. | [5 empty] | 48901 | 48901 | 48901 | 48901 |  | 48901 | 48901 | 48901 | °C | u8 | 1 | 0 | 10 | 5 | R/W
48902 | External ERS 1 accessory bypass temp. | [5 empty] | 48902 | 48902 | 48902 | 48902 |  | 48902 | 48902 | 48902 | °C | u8 | 1 | 2 | 10 | 4 | R/W
48904 | Pool Pump Type | [11 empty] | 48904 | 48904 |  | u8 | 1 | 0 | 1 | 0 | R/W
48905 | External cooling accessory Pump Type | [10 empty] | 48905 | 48905 | 48905 |  | u8 | 1 | 0 | 1 | 0 | R/W
48908 | Energy Meter Factor X23 | Energy meter factor X23, energy per pulse |  |  | 48908 | 48908 | 48908 | 48908 | 48908 | 48908 |  | 48908 | 48908 | 48908 | Wh | u16 | 1 | 1 | 10000 | 1000 | R/W
48909 | Energy Meter Factor X22 | Energy meter factor X22, energy per pulse |  |  | 48909 | 48909 | 48909 | 48909 | 48909 | 48909 |  | 48909 | 48909 | 48909 | Wh | u16 | 1 | 1 | 10000 | 1000 | R/W
48910 | Energy Meter X23 | Activates the external energy meter |  |  | 48910 | 48910 | 48910 | 48910 | 48910 | 48910 |  | 48910 | 48910 | 48910 |  | u8 | 1 | 0 | 1 | 0 | R/W
48911 | Energy Meter X22 | Activates the external energy meter |  |  | 48911 | 48911 | 48911 | 48911 | 48911 | 48911 |  | 48911 | 48911 | 48911 |  | u8 | 1 | 0 | 1 | 0 | R/W
48914 | Max int add. power, SG Ready |  |  |  | 48914 | 48914 | [6 empty] | 48914 | 48914 | kW | s16 | 100 | 0 | 4500 | 650 | R/W
48915 | Real air flow | Externally measured air flow during ventilation adjustments. |  |  | 48915 | 48915 | [9 empty] | s16 | 1 | 70 | 400 | -32768 | R/W
48918 | Limit humidity in room, cooling S8 | Limit humidity in room, cooling |  |  |  |  | 48918 | 48918 | 48918 | 48918 |  | 48918 | 48918 | 48918 |  | s8 | 1 | 0 | 0 | 0 | R/W
48919 | Limit humidity in room, cooling S7 | Limit humidity in room, cooling |  |  |  |  | 48919 | 48919 | 48919 | 48919 |  | 48919 | 48919 | 48919 |  | s8 | 1 | 0 | 0 | 0 | R/W
48920 | Limit humidity in room, cooling S6 | Limit humidity in room, cooling |  |  |  |  | 48920 | 48920 | 48920 | 48920 |  | 48920 | 48920 | 48920 |  | s8 | 1 | 0 | 0 | 0 | R/W
48921 | Limit humidity in room, cooling S5 | Limit humidity in room, cooling |  |  |  |  | 48921 | 48921 | 48921 | 48921 |  | 48921 | 48921 | 48921 |  | s8 | 1 | 0 | 0 | 0 | R/W
48922 | Limit humidity in room, cooling S4 | Limit humidity in room, cooling |  |  |  |  | 48922 | 48922 | 48922 | 48922 |  | 48922 | 48922 | 48922 |  | s8 | 1 | 0 | 0 | 0 | R/W
48923 | Limit humidity in room, cooling S3 | Limit humidity in room, cooling |  |  |  |  | 48923 | 48923 | 48923 | 48923 |  | 48923 | 48923 | 48923 |  | s8 | 1 | 0 | 0 | 0 | R/W
48924 | Limit humidity in room, cooling S2 | Limit humidity in room, cooling |  |  |  |  | 48924 | 48924 | 48924 | 48924 |  | 48924 | 48924 | 48924 |  | s8 | 1 | 0 | 0 | 0 | R/W
48925 | Limit humidity in room, cooling S1 | Limit humidity in room, cooling |  |  |  |  | 48925 | 48925 | 48925 | 48925 |  | 48925 | 48925 | 48925 |  | s8 | 1 | 0 | 0 | 0 | R/W
48926 | Humidity factor | Setting of how much the difference between set and actual room humidity should affect the supply temperature. | 48926 | 48926 | 48926 | 48926 | 48926 | 48926 | 48926 | 48926 | 48926 | 48926 | 48926 | 48926 |  | u8 | 10 | 5 | 100 | 10 | R/W
48927 | Humidity cool factor | Setting of how much the difference between set and actual room humidity should affect the supply temperature in cooling mode. | 48927 | 48927 | 48927 | 48927 | 48927 | 48927 | 48927 | 48927 | 48927 | 48927 | 48927 | 48927 |  | u8 | 10 | 0 | 0 | 0 | R/W
48928 | OPT Hystereses | The hystereses in OPT system |  |  |  |  | 48928 | 48928 | 48928 | 48928 |  | 48928 | 48928 | 48928 |  | s16 | 1 | 10 | 2000 | 100 | R/W
48930 | EME10 Activated | 0=not activated, 1=activated | 48930 | 48930 | 48930 | 48930 | 48930 | 48930 | [7 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48931 | EME PV Panel Affect Heating | 0=not affecting, 1=affecting | 48931 | 48931 | 48931 | 48931 | 48931 | 48931 | 48931 | 48931 | 48931 | 48931 | 48931 | 48931 |  | u8 | 1 | 0 | 1 | 0 | R/W
48932 | EME PV Panel Affect Hot Water | 0=not affecting, 1=affecting | 48932 | 48932 | 48932 | 48932 | 48932 | 48932 | 48932 | 48932 | 48932 | 48932 | 48932 | 48932 |  | u8 | 1 | 0 | 1 | 0 | R/W
48944 | Low brine out temp.EP15 | [7 empty] | 48944 | 48944 |  |  |  |  | °C | s16 | 10 | -120 | 150 | -80 | R/W
48947 | Outdoor Air Fan Speed, high temp. |  |  |  |  | 48947 | [8 empty] | % | u8 | 1 | 0 | 100 | 35 | R/W
48948 | FLM pump 4 | Operating mode for the FLM pump 4 |  |  |  |  | 48948 | 48948 | 48948 | 48948 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48949 | FLM pump 3 | Operating mode for the FLM pump 3 |  |  |  |  | 48949 | 48949 | 48949 | 48949 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48950 | FLM pump 2 | Operating mode for the FLM pump 2 |  |  |  |  | 48950 | 48950 | 48950 | 48950 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48951 | FLM 4 defrost | Minimum time between defrost in FLM 4 |  |  |  |  | 48951 | 48951 | 48951 | 48951 |  |  |  |  | hrs | u8 | 1 | 1 | 30 | 10 | R/W
48952 | FLM 3 defrost | Minimum time between defrost in FLM 3 |  |  |  |  | 48952 | 48952 | 48952 | 48952 |  |  |  |  | hrs | u8 | 1 | 1 | 30 | 10 | R/W
48953 | FLM 2 defrost | Minimum time between defrost in FLM 2 |  |  |  |  | 48953 | 48953 | 48953 | 48953 |  |  |  |  | hrs | u8 | 1 | 1 | 30 | 10 | R/W
48954 | FLM 4 cooling | FLM 4 cooling activated |  |  |  |  | 48954 | 48954 | 48954 | 48954 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48955 | FLM 3 cooling | FLM 3 cooling activated |  |  |  |  | 48955 | 48955 | 48955 | 48955 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48956 | FLM 2 cooling | FLM 2 cooling activated |  |  |  |  | 48956 | 48956 | 48956 | 48956 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48957 | FLM 4 pump speed | FLM 4 pump speed |  |  |  |  | 48957 | 48957 | 48957 | 48957 | [5 empty] | u8 | 1 | 1 | 100 | 100 | R/W
48958 | FLM 3 pump speed | FLM 3 pump speed |  |  |  |  | 48958 | 48958 | 48958 | 48958 | [5 empty] | u8 | 1 | 1 | 100 | 100 | R/W
48959 | FLM 2 pump speed | FLM 2 pump speed |  |  |  |  | 48959 | 48959 | 48959 | 48959 | [5 empty] | u8 | 1 | 1 | 100 | 100 | R/W
48960 | FLM 1 pump speed | FLM 1 pump speed |  |  |  |  | 48960 | 48960 | 48960 | 48960 | [5 empty] | u8 | 1 | 1 | 100 | 100 | R/W
48961 | FLM 4 over temp | Over temp for cooling active, when using FLM cooling |  |  |  |  | 48961 | 48961 | 48961 | 48961 |  |  |  |  | °C | u8 | 10 | 10 | 100 | 30 | R/W
48962 | FLM 3 over temp | Over temp for cooling active, when using FLM cooling |  |  |  |  | 48962 | 48962 | 48962 | 48962 |  |  |  |  | °C | u8 | 10 | 10 | 100 | 30 | R/W
48963 | FLM 2 over temp | Over temp for cooling active, when using FLM cooling |  |  |  |  | 48963 | 48963 | 48963 | 48963 |  |  |  |  | °C | u8 | 10 | 10 | 100 | 30 | R/W
48964 | FLM 1 over temp | Over temp for cooling active, when using FLM cooling |  |  |  |  | 48964 | 48964 | 48964 | 48964 |  |  |  |  | °C | u8 | 10 | 10 | 100 | 30 | R/W
48965 | FLM 4 set point, cooling | Set point, cooling, when using FLM cooling |  |  |  |  | 48965 | 48965 | 48965 | 48965 |  |  |  |  | °C | s16 | 10 | 50 | 400 | 210 | R/W
48966 | FLM 3 set point, cooling | Set point, cooling, when using FLM cooling |  |  |  |  | 48966 | 48966 | 48966 | 48966 |  |  |  |  | °C | s16 | 10 | 50 | 400 | 210 | R/W
48967 | FLM 2 set point, cooling | Set point, cooling, when using FLM cooling |  |  |  |  | 48967 | 48967 | 48967 | 48967 |  |  |  |  | °C | s16 | 10 | 50 | 400 | 210 | R/W
48968 | FLM 1 set point, cooling | Set point, cooling, when using FLM cooling | 48968 | 48968 | 48968 | 48968 | 48968 | 48968 | 48968 | 48968 | 48968 | 48968 | 48968 | 48968 | °C | s16 | 10 | 50 | 400 | 210 | R/W
48969 | AUX block OPT | AUX block OPT |  |  | 48969 |  | 48969 | 48969 | 48969 | 48969 |  | 48969 | 48969 | 48969 |  | u8 | 1 | 0 | 0 | 0 | R/W
48970 | Outdoor Air Mixing function | Activates the Outdoor Air Mixing function. | 48970 | 48970 | 48970 | 48970 | 48970 | 48970 | 48970 | 48970 | 48970 | 48970 | 48970 | 48970 |  | u8 | 1 | 0 | 1 | 0 | R/W
48971 | Outdoor air max. temp. | Maximum outdoor air temperature set. |  |  |  | 48971 | [9 empty] | s8 | 1 | 0 | 40 | 10 | R/W
48972 | Outdoor air min. temp. | Minimum outdoor air temperature set. |  |  | 48972 | 48972 | [9 empty] | s8 | 1 | -10 | 10 | -5 | R/W
48973 | Reduced ventilation | Outdoor air reduced ventilation. 0 = deactivated, 1 = activated. |  |  | 48973 | 48973 | [9 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48974 | High outdoor air temperature | Above this limit the ventilation is reduced. |  |  |  | 48974 | [8 empty] | °C | s16 | 1 | 20 | 50 | 25 | R/W
48975 | OEK accessory | Activates the OEK Accessory. |  |  | 48975 | 48975 | [9 empty] | u8 | 1 | 0 | 1 | 0 | R/W
48976 | Smart home room control |  | 48976 | 48976 | 48976 | 48976 | 48976 | 48976 | 48976 | 48976 | 48976 | 48976 | 48976 | 48976 |  | u8 | 1 | 0 | 1 | 0 | R/W
48977 | Speed brine pump wait mode | [5 empty] | 48977 | 48977 | 48977 | 48977 |  |  |  |  | % | u8 | 1 | 0 | 100 | 30 | R/W
48979 | Smart energy source | Smart energy source activated. |  |  |  |  | 48979 | 48979 | 48979 | 48979 |  | 48979 | 48979 | 48979 |  | u8 | 1 | 0 | 1 | 0 | R/W
48980 | Smart energy source, ctrl method | Smart energy source, ctrl method. 0 = price. 1 = primary factor. |  |  |  |  | 48980 | 48980 | 48980 | 48980 |  | 48980 | 48980 | 48980 |  | u8 | 1 | 0 | 1 | 0 | R/W
48981 | Smart energy source, electricity price source | Smart energy source, electricity price source. 0 = fixed price. 1 = tariff. 2= spot price. |  |  |  |  | 48981 | 48981 | 48981 | 48981 |  | 48981 | 48981 | 48981 |  | u8 | 1 | 0 | 2 | 0 | R/W
48982 | Smart energy source, electricity price | Smart energy source, electricity fixed price. |  |  |  |  | 48982 | 48982 | 48982 | 48982 |  | 48982 | 48982 | 48982 |  | u16 | 1 | 0 | 10000 | 100 | R/W
48983 | Smart energy source, fixed elec. price from | Smart energy source, fixed electricity price part source, if spot electricity price are used. 0 = fixed price. 1 = tariff. |  |  |  |  | 48983 | 48983 | 48983 | 48983 |  | 48983 | 48983 | 48983 |  | u8 | 1 | 0 | 1 | 0 | R/W
48984 | Smart energy source, fixed part electricity price | Smart energy source, fixed part (if spot price are used) electricity price |  |  |  |  | 48984 | 48984 | 48984 | 48984 |  | 48984 | 48984 | 48984 |  | u16 | 1 | 0 | 10000 | 100 | R/W
48985 | Smart energy source, shunt add price source | Smart energy source, shunted addition price part source. From tariff or fixed price. 0 = fixed price. 1 = tariff. |  |  |  |  | 48985 | 48985 | 48985 | 48985 |  | 48985 | 48985 | 48985 |  | u8 | 1 | 0 | 1 | 0 | R/W
48986 | Smart energy source, shunt add price | Smart energy source, shunted add price |  |  |  |  | 48986 | 48986 | 48986 | 48986 |  | 48986 | 48986 | 48986 |  | u16 | 1 | 0 | 10000 | 100 | R/W
48987 | Smart energy source, ext step add price from | Smart energy source, external step add source. From tariff or fixed price. 0 = fixed price. 1 = tariff. |  |  |  |  | 48987 | 48987 | 48987 | 48987 |  | 48987 | 48987 | 48987 |  | u8 | 1 | 0 | 1 | 0 | R/W
48988 | Smart energy source, ext step add price | Smart energy source, ext step add price |  |  |  |  | 48988 | 48988 | 48988 | 48988 |  | 48988 | 48988 | 48988 |  | u16 | 1 | 0 | 10000 | 100 | R/W
48989 | Smart energy source, OPT10 price source | Smart energy source, OPT10 addition price source. 0 = fixed price. 1 = tariff. |  |  |  |  | 48989 | 48989 | 48989 | 48989 |  | 48989 | 48989 | 48989 |  | u8 | 1 | 0 | 1 | 0 | R/W
48990 | Smart energy source, OPT10 price | Smart energy source, OPT10 addition price. |  |  |  |  | 48990 | 48990 | 48990 | 48990 |  | 48990 | 48990 | 48990 |  | u16 | 1 | 0 | 10000 | 100 | R/W
48991 | Smart energy source, primary factor elec. | Smart energy source, primary factor electricity |  |  |  |  | 48991 | 48991 | 48991 | 48991 |  | 48991 | 48991 | 48991 |  | u8 | 10 | 0 | 50 | 25 | R/W
48992 | Smart energy source, primary factor shunted add. | Smart energy source, primary factor shunted addition |  |  |  |  | 48992 | 48992 | 48992 | 48992 |  | 48992 | 48992 | 48992 |  | u8 | 10 | 0 | 50 | 10 | R/W
48993 | Smart energy source, primary factor ext step add | Smart energy source, primary factor external step addition |  |  |  |  | 48993 | 48993 | 48993 | 48993 |  | 48993 | 48993 | 48993 |  | u8 | 10 | 0 | 50 | 10 | R/W
48994 | Smart energy source, primary factor OPT10 add. | Smart energy source, primary factor OPT10 addition |  |  |  |  | 48994 | 48994 | 48994 | 48994 |  | 48994 | 48994 | 48994 |  | u8 | 10 | 0 | 50 | 10 | R/W
48995 | Smart energy source, OPT10 high tariff price | Smart energy source, OPT10 addition high tariff price |  |  |  |  | 48995 | 48995 | 48995 | 48995 |  | 48995 | 48995 | 48995 |  | u16 | 1 | 1 | 10000 | 100 | R/W
48996 | Smart energy source, OPT10 low tariff price | Smart energy source, OPT10 addition low tariff price |  |  |  |  | 48996 | 48996 | 48996 | 48996 |  | 48996 | 48996 | 48996 |  | u16 | 1 | 1 | 10000 | 100 | R/W
48997 | Smart energy source, ext step add high tariff price | Smart energy source, external step addition high tariff price |  |  |  |  | 48997 | 48997 | 48997 | 48997 |  | 48997 | 48997 | 48997 |  | u16 | 1 | 1 | 10000 | 100 | R/W
48998 | Smart energy source, ext step add low tariff price | Smart energy source, external step addition low tariff price |  |  |  |  | 48998 | 48998 | 48998 | 48998 |  | 48998 | 48998 | 48998 |  | u16 | 1 | 1 | 10000 | 100 | R/W
48999 | Smart energy source, shunt add high tariff price | Smart energy source, shunt addition high tariff price |  |  |  |  | 48999 | 48999 | 48999 | 48999 |  | 48999 | 48999 | 48999 |  | u16 | 1 | 1 | 10000 | 100 | R/W
49000 | Smart energy source, shunt add low tariff price | Smart energy source, shunt addition low tariff price |  |  |  |  | 49000 | 49000 | 49000 | 49000 |  | 49000 | 49000 | 49000 |  | u16 | 1 | 1 | 10000 | 100 | R/W
49001 | Smart energy source, fixed elec. high tariff price | Smart energy source, fixed electricity part high tariff price |  |  |  |  | 49001 | 49001 | 49001 | 49001 |  | 49001 | 49001 | 49001 |  | u16 | 1 | 1 | 10000 | 100 | R/W
49002 | Smart energy source, fixed elec. low tariff price | Smart energy source, fixed electricity part low tariff price |  |  |  |  | 49002 | 49002 | 49002 | 49002 |  | 49002 | 49002 | 49002 |  | u16 | 1 | 1 | 10000 | 100 | R/W
49003 | Smart energy source, electricity high tariff price | Smart energy source, electricity high tariff price |  |  |  |  | 49003 | 49003 | 49003 | 49003 |  | 49003 | 49003 | 49003 |  | u16 | 1 | 1 | 10000 | 100 | R/W
49004 | Smart energy source, electricity high low price | Smart energy source, electricity low tariff price |  |  |  |  | 49004 | 49004 | 49004 | 49004 |  | 49004 | 49004 | 49004 |  | u16 | 1 | 1 | 10000 | 100 | R/W
49005 | Smart energy source, DM diff source prio 5 | Smart energy source, DM diff source with prio 5 |  |  |  |  | 49005 | 49005 | 49005 | 49005 |  | 49005 | 49005 | 49005 |  | s16 | 1 | 100 | 2000 | 400 | R/W
49006 | Smart energy source, DM diff source prio 4 | Smart energy source, DM diff source with prio 4 |  |  |  |  | 49006 | 49006 | 49006 | 49006 |  | 49006 | 49006 | 49006 |  | s16 | 1 | 100 | 2000 | 400 | R/W
49007 | Smart energy source, DM diff source prio 3 | Smart energy source, DM diff source with prio 3 |  |  |  |  | 49007 | 49007 | 49007 | 49007 |  | 49007 | 49007 | 49007 |  | s16 | 1 | 100 | 2000 | 400 | R/W
49008 | Smart energy source, DM diff source prio 2 | Smart energy source, DM diff source with prio 2 |  |  |  |  | 49008 | 49008 | 49008 | 49008 |  | 49008 | 49008 | 49008 |  | s16 | 1 | 100 | 2000 | 400 | R/W
49009 | Smart energy source, DM start source prio 1 | Smart energy source, DM start source with prio 1 |  |  |  |  | 49009 | 49009 | 49009 | 49009 |  | 49009 | 49009 | 49009 |  | s16 | 1 | -2000 | -10 | -60 | R/W
49190 | Ground water pump temp alarm | Ground water pump temperature alarm |  |  |  |  | 49190 | 49190 | 49190 | 49190 | [5 empty] | u8 | 1 | 0 | 1 | 0 | R/W
49191 | Ground water pump temp alarm level | Ground water pump temperature alarm level |  |  |  |  | 49191 | 49191 | 49191 | 49191 |  |  |  |  | °C | s8 | 1 | -15 | 20 | 3 | R/W
49192 | Fixed delta t, brine pump | [5 empty] | 49192 | 49192 | 49192 | 49192 |  |  |  |  | °C | u8 | 1 | 2 | 10 | 4 | R/W
49193 | Brine pump auto controlled | Brine pump auto controlled, 0= manual, 1 = auto controlled, 2 = fixed delta controlled |  |  |  |  | 49193 | 49193 | 49193 | 49193 | [5 empty] | s8 | 1 | 0 | 2 | 1 | R/W
49208 | Max diff. SES prio 1. | [11 empty] | 49208 | 49208 | °C | s16 | 10 | 10 | 250 | 100 | R/W
49209 | Max diff. SES.other prios | [11 empty] | 49209 | 49209 | °C | s16 | 10 | 10 | 250 | 70 | R/W
49221 | Delta brine pump passive cooling | [5 empty] | 49221 | 49221 | [6 empty] | °C | u8 | 1 | 1 | 15 | 4 | R/W
49223 | SCA solar heating | SCA solar heating: 0=not activated, 1=activated |  |  | 49223 | 49223 | [9 empty] | u8 | 1 | 0 | 1 | 0 | R/W
49224 | SCA ext. hot water | SCA external hot water: 0=not activated, 1=activated |  |  | 49224 | 49224 | [9 empty] | u8 | 1 | 0 | 1 | 0 | R/W
49225 | max add power | max addition power | [10 empty] | 49225 |  | kW | s16 | 100 | 250 | 2500 | 2500 | R/W
49226 | OPT Gas Type | 0 = G20/G25, 1 = G31 | [10 empty] | 49226 |  |  | u8 | 1 | 0 | 1 | 0 | R/W
49227 | Block top frequencies | Block compressor top frequencies |  |  | 49227 | 49227 | [8 empty] | Hz | u8 | 1 | 0 | 1 | 0 | R/W
49228 | DM start value EP15. | The value the degree minutes needed to be reached for the pump to start heating with EP15 | [6 empty] | 49228 | [6 empty] | s16 | 1 | -1000 | -30 | -60 | R/W
49229 | DM start value EP14 | The value the degree minutes needed to be reached for the pump to start heating with EP14 | [6 empty] | 49229 | [6 empty] | s16 | 1 | -1000 | -30 | -200 | R/W
49230 | Internal HW add in tank, use in heat | Internal HW add in tank, use in heat | [9 empty] | 49230 |  |  |  | u8 | 1 | 0 | 1 | 1 | R/W
49232 | EB108 Installed | [6 empty] | 49232 | 49232 | 49232 |  | 49232 |  |  |  | u8 | 1 | 0 | 1 | 0 | R
49233 | EB107 Installed | [6 empty] | 49233 | 49233 | 49233 |  | 49233 |  |  |  | u8 | 1 | 0 | 1 | 0 | R
49234 | EB106 Installed | [6 empty] | 49234 | 49234 | 49234 |  | 49234 |  |  |  | u8 | 1 | 0 | 1 | 0 | R
49235 | EB105 Installed | [6 empty] | 49235 | 49235 | 49235 |  | 49235 |  |  |  | u8 | 1 | 0 | 1 | 0 | R
49236 | EB104 Installed | [6 empty] | 49236 | 49236 | 49236 |  | 49236 |  |  |  | u8 | 1 | 0 | 1 | 0 | R
49237 | EB103 Installed | [6 empty] | 49237 | 49237 | 49237 |  | 49237 |  |  |  | u8 | 1 | 0 | 1 | 0 | R
49238 | EB102 Installed | [6 empty] | 49238 | 49238 | 49238 |  | 49238 |  |  |  | u8 | 1 | 0 | 1 | 0 | R
49239 | EB101 Installed | [5 empty] | 49239 | 49239 | 49239 | 49239 | 49239 | 49239 | 49239 | 49239 |  | u8 | 1 | 0 | 1 | 0 | R
49241 | External ERS 1 accessory bypass set temp. | [5 empty] | 49241 | 49241 | 49241 | 49241 |  | 49241 | 49241 | 49241 | °C | u8 | 1 | 5 | 30 | 25 | R/W
49242 | External ERS 1 accessory bypass at heat | [5 empty] | 49242 | 49242 | 49242 | 49242 |  | 49242 | 49242 | 49242 |  | u8 | 1 | 0 | 1 | 0 | R/W
49243 | Speed circ.pump HW EP15 | [7 empty] | 49243 | [5 empty] | % | u8 | 1 | 1 | 100 | 70 | R/W
49244 | Speed circ.pump Heat EP15 | [7 empty] | 49244 | [5 empty] | % | u8 | 1 | 1 | 100 | 70 | R/W
49245 | Speed circ.pump Pool EP15 | [7 empty] | 49245 | [5 empty] | % | u8 | 1 | 1 | 100 | 70 | R/W
49246 | Speed Circulation Pump Passive Cooling EP15 | [7 empty] | 49246 | [5 empty] | % | u8 | 1 | 1 | 100 | 70 | R/W
49247 | Speed Circulation Pump Active Cooling EP15 | [7 empty] | 49247 | [5 empty] | % | u8 | 1 | 1 | 100 | 70 | R/W
49248 | Speed brine pump EP15 | [7 empty] | 49248 | [5 empty] | % | u8 | 1 | 1 | 100 | 100 | R/W
49249 | Speed brine pump passive cooling EP15 | [7 empty] | 49249 | [5 empty] | % | u8 | 1 | 0 | 100 | 75 | R/W
49250 | Speed brine pump active cooling EP15 | [7 empty] | 49250 | [5 empty] | % | u8 | 1 | 0 | 100 | 75 | R/W
49251 | Waiting speed brine pump cooling EP15 | [7 empty] | 49251 | [5 empty] | % | u8 | 1 | 0 | 100 | 30 | R/W
49252 | Speed brine pump wait mode EP15 | [7 empty] | 49252 | [5 empty] | % | u8 | 1 | 0 | 100 | 30 | R/W
49277 | FLM 4 fan | FLM 4 fan |  |  |  |  | 49277 | 49277 | 49277 | 49277 | [5 empty] | u8 | 1 | 6 | 6 | 6 | R/W
49278 | FLM 3 fan | FLM 3 fan |  |  |  |  | 49278 | 49278 | 49278 | 49278 | [5 empty] | u8 | 1 | 6 | 6 | 6 | R/W
49279 | FLM 2 fan | FLM 2 fan |  |  |  |  | 49279 | 49279 | 49279 | 49279 | [5 empty] | u8 | 1 | 6 | 6 | 6 | R/W
49280 | FLM 1 fan | FLM 1 fan |  |  |  |  | 49280 | 49280 | 49280 | 49280 | [5 empty] | u8 | 1 | 6 | 6 | 6 | R/W
49281 | SAM fan model | SAM fan model |  |  | 49281 | [10 empty] | u8 | 1 | 6 | 6 | 6 | R/W
49282 | Silent Mode Max Speed |  |  |  | 49282 | 49282 | [8 empty] | Hz | u8 | 1 | 80 | 120 | 120 | R/W
49285 | Energy Meter pulses per kWh X23 | Energy meter factor X23, pulses per kWh |  |  | 49285 | 49285 | 49285 | 49285 | 49285 | 49285 |  | 49285 | 49285 | 49285 |  | u16 | 1 | 1 | 10000 | 500 | R/W
49286 | Energy Meter pulses per kWh X22 | Energy meter factor X22, pulses per kWh |  |  | 49286 | 49286 | 49286 | 49286 | 49286 | 49286 |  | 49286 | 49286 | 49286 |  | u16 | 1 | 1 | 10000 | 500 | R/W
49287 | Energy Meter mode X23 | Energy meter X23 in mode Wh/pulse = 0 or pulses/kWh = 1 |  |  | 49287 | 49287 | 49287 | 49287 | 49287 | 49287 |  | 49287 | 49287 | 49287 |  | u8 | 1 | 0 | 1 | 0 | R/W
49288 | Energy Meter mode X22 | Energy meter X22 in mode Wh/pulse = 0 or pulses/kWh = 1 |  |  | 49288 | 49288 | 49288 | 49288 | 49288 | 49288 |  | 49288 | 49288 | 49288 |  | u8 | 1 | 0 | 1 | 0 | R/W
49289 | Ground water pump speed control |  | 49289 | 49289 | 49289 | 49289 | 49289 | 49289 | 49289 | 49289 | 49289 | 49289 | 49289 | 49289 |  | s8 | 1 | 0 | 1 | 0 | R/W
49290 | Ground water pump auto speed control | Ground water pump auto speed control |  |  |  |  | 49290 | 49290 | 49290 | 49290 | [5 empty] | s8 | 1 | 0 | 1 | 1 | R/W
49291 | Ground water pump manual speed | Ground water pump temperature alarm level |  |  |  |  | 49291 | 49291 | 49291 | 49291 |  |  |  |  | % | u8 | 1 | 1 | 100 | 75 | R/W
49292 | Ground water pump control signal | Ground water pump control signal (0 = 0V-10V; 1= 10V-0V) |  |  |  |  | 49292 | 49292 | 49292 | 49292 | [5 empty] | s8 | 1 | 0 | 0 | 0 | R/W
49293 | Ground water pump min speed | Ground water pump voltage at min speed |  |  |  |  | 49293 | 49293 | 49293 | 49293 |  |  |  |  | V | u8 | 1 | 0 | 80 | 30 | R/W
49295 | AHPS External Addition start temperature. |  |  |  | 49295 | [9 empty] | °C | u8 | 1 | 40 | 55 | 50 | R/W
49296 | AHPS External Addition stop temperature. |  |  |  | 49296 | [9 empty] | °C | u8 | 1 | 44 | 59 | 54 | R/W
49297 | EME20 Activated | 0=not activated, 1=activated | 49297 | 49297 | 49297 | 49297 | 49297 | 49297 | 49297 | 49297 | 49297 | 49297 | 49297 | 49297 |  | u8 | 1 | 0 | 1 | 0 | R/W
49298 | EME PV Panel Affect Pool | 0=not affecting, 1=affecting | 49298 | 49298 | 49298 | 49298 | 49298 | 49298 | 49298 | 49298 |  | 49298 | 49298 | 49298 |  | u8 | 1 | 0 | 0 | 0 | R/W
49301 | Speed circ.pump add prio | [11 empty] | 49301 |  | % | u8 | 1 | 0 | 0 | 0 | R/W
49328 | ERS 4 Exhaust Fan speed 4 | [5 empty] | 49328 | 49328 | 49328 | 49328 |  | 49328 | 49328 | 49328 | % | u8 | 1 | 0 | 100 | 100 | R/W
49329 | ERS 3 Exhaust Fan speed 4 | [5 empty] | 49329 | 49329 | 49329 | 49329 |  | 49329 | 49329 | 49329 | % | u8 | 1 | 0 | 100 | 100 | R/W
49330 | ERS 2 Exhaust Fan speed 4 | [5 empty] | 49330 | 49330 | 49330 | 49330 |  | 49330 | 49330 | 49330 | % | u8 | 1 | 0 | 100 | 100 | R/W
49331 | ERS 4 Exhaust Fan speed 3 | [5 empty] | 49331 | 49331 | 49331 | 49331 |  | 49331 | 49331 | 49331 | % | u8 | 1 | 0 | 100 | 80 | R/W
49332 | ERS 3 Exhaust Fan speed 3 | [5 empty] | 49332 | 49332 | 49332 | 49332 |  | 49332 | 49332 | 49332 | % | u8 | 1 | 0 | 100 | 80 | R/W
49333 | ERS 2 Exhaust Fan speed 3 | [5 empty] | 49333 | 49333 | 49333 | 49333 |  | 49333 | 49333 | 49333 | % | u8 | 1 | 0 | 100 | 80 | R/W
49334 | ERS 4 Exhaust Fan speed 2 | [5 empty] | 49334 | 49334 | 49334 | 49334 |  | 49334 | 49334 | 49334 | % | u8 | 1 | 0 | 100 | 30 | R/W
49335 | ERS 3 Exhaust Fan speed 2 | [5 empty] | 49335 | 49335 | 49335 | 49335 |  | 49335 | 49335 | 49335 | % | u8 | 1 | 0 | 100 | 30 | R/W
49336 | ERS 2 Exhaust Fan speed 2 | [5 empty] | 49336 | 49336 | 49336 | 49336 |  | 49336 | 49336 | 49336 | % | u8 | 1 | 0 | 100 | 30 | R/W
49337 | ERS 4 Exhaust Fan speed 1 | [5 empty] | 49337 | 49337 | 49337 | 49337 |  | 49337 | 49337 | 49337 | % | u8 | 1 | 0 | 100 | 0 | R/W
49338 | ERS 3 Exhaust Fan speed 1 | [5 empty] | 49338 | 49338 | 49338 | 49338 |  | 49338 | 49338 | 49338 | % | u8 | 1 | 0 | 100 | 0 | R/W
49339 | ERS 2 Exhaust Fan speed 1 | [5 empty] | 49339 | 49339 | 49339 | 49339 |  | 49339 | 49339 | 49339 | % | u8 | 1 | 0 | 100 | 0 | R/W
49340 | ERS 4 Exhaust Fan speed normal | [5 empty] | 49340 | 49340 | 49340 | 49340 |  | 49340 | 49340 | 49340 | % | u8 | 1 | 1 | 100 | 75 | R/W
49341 | ERS 3 Exhaust Fan speed normal | [5 empty] | 49341 | 49341 | 49341 | 49341 |  | 49341 | 49341 | 49341 | % | u8 | 1 | 1 | 100 | 75 | R/W
49342 | ERS 2 Exhaust Fan speed normal | [5 empty] | 49342 | 49342 | 49342 | 49342 |  | 49342 | 49342 | 49342 | % | u8 | 1 | 1 | 100 | 75 | R/W
49343 | ERS 4 Supply Fan speed 4 | [5 empty] | 49343 | 49343 | 49343 | 49343 |  | 49343 | 49343 | 49343 | % | u8 | 1 | 0 | 100 | 100 | R/W
49344 | ERS 3 Supply Fan speed 4 | [5 empty] | 49344 | 49344 | 49344 | 49344 |  | 49344 | 49344 | 49344 | % | u8 | 1 | 0 | 100 | 100 | R/W
49345 | ERS 2 Supply Fan speed 4 | [5 empty] | 49345 | 49345 | 49345 | 49345 |  | 49345 | 49345 | 49345 | % | u8 | 1 | 0 | 100 | 100 | R/W
49346 | ERS 4 Supply Fan speed 3 | [5 empty] | 49346 | 49346 | 49346 | 49346 |  | 49346 | 49346 | 49346 | % | u8 | 1 | 0 | 100 | 80 | R/W
49347 | ERS 3 Supply Fan speed 3 | [5 empty] | 49347 | 49347 | 49347 | 49347 |  | 49347 | 49347 | 49347 | % | u8 | 1 | 0 | 100 | 80 | R/W
49348 | ERS 2 Supply Fan speed 3 | [5 empty] | 49348 | 49348 | 49348 | 49348 |  | 49348 | 49348 | 49348 | % | u8 | 1 | 0 | 100 | 80 | R/W
49349 | ERS 4 Supply Fan speed 2 | [5 empty] | 49349 | 49349 | 49349 | 49349 |  | 49349 | 49349 | 49349 | % | u8 | 1 | 0 | 100 | 30 | R/W
49350 | ERS 3 Supply Fan speed 2 | [5 empty] | 49350 | 49350 | 49350 | 49350 |  | 49350 | 49350 | 49350 | % | u8 | 1 | 0 | 100 | 30 | R/W
49351 | ERS 2 Supply Fan speed 2 | [5 empty] | 49351 | 49351 | 49351 | 49351 |  | 49351 | 49351 | 49351 | % | u8 | 1 | 0 | 100 | 30 | R/W
49352 | ERS 4 Supply Fan speed 1 | [5 empty] | 49352 | 49352 | 49352 | 49352 |  | 49352 | 49352 | 49352 | % | u8 | 1 | 0 | 100 | 0 | R/W
49353 | ERS 3 Supply Fan speed 1 | [5 empty] | 49353 | 49353 | 49353 | 49353 |  | 49353 | 49353 | 49353 | % | u8 | 1 | 0 | 100 | 0 | R/W
49354 | ERS 2 Supply Fan speed 1 | [5 empty] | 49354 | 49354 | 49354 | 49354 |  | 49354 | 49354 | 49354 | % | u8 | 1 | 0 | 100 | 0 | R/W
49355 | ERS 4 Supply Fan speed normal | [5 empty] | 49355 | 49355 | 49355 | 49355 |  | 49355 | 49355 | 49355 | % | u8 | 1 | 1 | 100 | 75 | R/W
49356 | ERS 3 Supply Fan speed normal | [5 empty] | 49356 | 49356 | 49356 | 49356 |  | 49356 | 49356 | 49356 | % | u8 | 1 | 1 | 100 | 75 | R/W
49357 | ERS 2 Supply Fan speed normal | [5 empty] | 49357 | 49357 | 49357 | 49357 |  | 49357 | 49357 | 49357 | % | u8 | 1 | 1 | 100 | 75 | R/W
49358 | Night cooling | If the fan should have a higher speed when there is a high room temp and a low outdoor temp. | 49358 | 49358 | 49358 | 49358 | 49358 | 49358 | 49358 | 49358 |  | 49358 | 49358 | 49358 |  | u8 | 1 | 0 | 1 | 0 | R/W
49359 | Night cooling | If the fan should have a higher speed when there is a high room temp and a low outdoor temp. | 49359 | 49359 | 49359 | 49359 | 49359 | 49359 | 49359 | 49359 |  | 49359 | 49359 | 49359 |  | u8 | 1 | 0 | 1 | 0 | R/W
49360 | Night cooling | If the fan should have a higher speed when there is a high room temp and a low outdoor temp. | 49360 | 49360 | 49360 | 49360 | 49360 | 49360 | 49360 | 49360 |  | 49360 | 49360 | 49360 |  | u8 | 1 | 0 | 1 | 0 | R/W
49361 | Start room temp. night cooling |  | 49361 | 49361 | 49361 | 49361 | 49361 | 49361 | 49361 | 49361 |  | 49361 | 49361 | 49361 | °C | u8 | 1 | 20 | 30 | 25 | R/W
49362 | Start room temp. night cooling |  | 49362 | 49362 | 49362 | 49362 | 49362 | 49362 | 49362 | 49362 |  | 49362 | 49362 | 49362 | °C | u8 | 1 | 20 | 30 | 25 | R/W
49363 | Start room temp. night cooling |  | 49363 | 49363 | 49363 | 49363 | 49363 | 49363 | 49363 | 49363 |  | 49363 | 49363 | 49363 | °C | u8 | 1 | 20 | 30 | 25 | R/W
49364 | Night Cooling Min. diff. | Minimum difference between room temp and outdoor temp to start night cooling | 49364 | 49364 | 49364 | 49364 | 49364 | 49364 | 49364 | 49364 |  | 49364 | 49364 | 49364 | °C | u8 | 1 | 3 | 10 | 6 | R/W
49365 | Night Cooling Min. diff. | Minimum difference between room temp and outdoor temp to start night cooling | 49365 | 49365 | 49365 | 49365 | 49365 | 49365 | 49365 | 49365 |  | 49365 | 49365 | 49365 | °C | u8 | 1 | 3 | 10 | 6 | R/W
49366 | Night Cooling Min. diff. | Minimum difference between room temp and outdoor temp to start night cooling | 49366 | 49366 | 49366 | 49366 | 49366 | 49366 | 49366 | 49366 |  | 49366 | 49366 | 49366 | °C | u8 | 1 | 3 | 10 | 6 | R/W
49367 | ERS 4 accessory | Activates the ERS accessory |  |  |  |  | 49367 | 49367 | 49367 | 49367 |  | 49367 | 49367 | 49367 |  | u8 | 1 | 0 | 1 | 0 | R/W
49368 | ERS 3 accessory | Activates the ERS accessory |  |  |  |  | 49368 | 49368 | 49368 | 49368 |  | 49368 | 49368 | 49368 |  | u8 | 1 | 0 | 1 | 0 | R/W
49369 | ERS 2 accessory | Activates the ERS accessory |  |  |  |  | 49369 | 49369 | 49369 | 49369 |  | 49369 | 49369 | 49369 |  | u8 | 1 | 0 | 1 | 0 | R/W
49370 | External ERS 4 accessory min exhaust temp. | [5 empty] | 49370 | 49370 | 49370 | 49370 |  | 49370 | 49370 | 49370 | °C | u8 | 1 | 0 | 10 | 5 | R/W
49371 | External ERS 3 accessory min exhaust temp. | [5 empty] | 49371 | 49371 | 49371 | 49371 |  | 49371 | 49371 | 49371 | °C | u8 | 1 | 0 | 10 | 5 | R/W
49372 | External ERS 2 accessory min exhaust temp. | [5 empty] | 49372 | 49372 | 49372 | 49372 |  | 49372 | 49372 | 49372 | °C | u8 | 1 | 0 | 10 | 5 | R/W
49373 | External ERS 4 accessory bypass temp. | [5 empty] | 49373 | 49373 | 49373 | 49373 |  | 49373 | 49373 | 49373 | °C | u8 | 1 | 2 | 10 | 4 | R/W
49374 | External ERS 3 accessory bypass temp. | [5 empty] | 49374 | 49374 | 49374 | 49374 |  | 49374 | 49374 | 49374 | °C | u8 | 1 | 2 | 10 | 4 | R/W
49375 | External ERS 2 accessory bypass temp. | [5 empty] | 49375 | 49375 | 49375 | 49375 |  | 49375 | 49375 | 49375 | °C | u8 | 1 | 2 | 10 | 4 | R/W
49376 | External ERS 4 accessory bypass set temp. | [5 empty] | 49376 | 49376 | 49376 | 49376 |  | 49376 | 49376 | 49376 | °C | u8 | 1 | 5 | 30 | 25 | R/W
49377 | External ERS 3 accessory bypass set temp. | [5 empty] | 49377 | 49377 | 49377 | 49377 |  | 49377 | 49377 | 49377 | °C | u8 | 1 | 5 | 30 | 25 | R/W
49378 | External ERS 2 accessory bypass set temp. | [5 empty] | 49378 | 49378 | 49378 | 49378 |  | 49378 | 49378 | 49378 | °C | u8 | 1 | 5 | 30 | 25 | R/W
49379 | External ERS 4 accessory bypass at heat | [5 empty] | 49379 | 49379 | 49379 | 49379 |  | 49379 | 49379 | 49379 |  | u8 | 1 | 0 | 1 | 0 | R/W
49380 | External ERS 3 accessory bypass at heat | [5 empty] | 49380 | 49380 | 49380 | 49380 |  | 49380 | 49380 | 49380 |  | u8 | 1 | 0 | 1 | 0 | R/W
49381 | External ERS 2 accessory bypass at heat | [5 empty] | 49381 | 49381 | 49381 | 49381 |  | 49381 | 49381 | 49381 |  | u8 | 1 | 0 | 1 | 0 | R/W
49430 | AUX ERS Fire Place Guard | Activates ERS Fire Place Guard |  |  |  |  | 49430 | 49430 | 49430 | 49430 |  | 49430 | 49430 | 49430 |  | u8 | 1 | 0 | 0 | 0 | R/W
49431 | Stop Temperature Supply Air Heating | Stop temperature for supply air heating | 49431 | 49431 | [10 empty] | °C | s16 | 1 | 100 | 400 | 170 | R/W